## User Input
|  |  |  | ELEVATED WATER TOWER |  |  |  | LIT-03 | [6 empty] | LIT-02 |  | FIT-105
[9 empty] | % |  |  |  |  | CLEARWELL |  | % |  | L/s
[5 empty] | Baffling |  | 0.1
FRC-01 |  | TEM-01 | [6 empty] | FRC-02 |  | FIT-102
| mg/L |  | oC | [6 empty] | mg/L |  | L/s
PH-02
FIT-106 |  | PH-03
L/s
TO DISTRIBUTION | [13 empty] | Baffling | 0.1
A Filtration Credit can been applied for use in calculating total reduction of Giardia and Viruses. In order to be considered conventional filtration and claim the 2.5 log Giardia cyst removal and 2 log virus removal credit, the filtration process must meet the following criteria: * use a chemical coagulant at all times when the treatment plant is in operation; * monitor and adjust chemical dosages in response to variations in raw water quality; * maintain effective backwash procedures, including filter-to-waste or an equivalent procedure during filter ripening to ensure that the effluent turbidity requirements are met at all times; * continuously monitor filtrate turbidity from each filter; and * meet the performance criterion for filtered water turbidity of less than or equal to 0.3 NTU in 95% of the measurements each month. When this Filtration Credit is being met, the target Log-Inactivation for this CT Calculator is 0.5 for Giardia, and 2 for Viruses.
| Summary of Inactivation Credits | [8 empty] | Target Log-Inactivation
[5 empty] | Giardia | Viruses |  |  |  | Giardia | 0.5
| CT Achieved |  |  |  | #DIV/0! | #DIV/0! |  |  |  | Viruses | 2
| CT Required |  |  |  | #DIV/0! | #DIV/0!
| Log Inactivation |  |  |  | #VALUE! | #DIV/0!
PUMP1
PUMP2
PUMP3

## Release Notes (hidden)
Release Notes for Niagara Falls CT Calculator Version 1.1
These notes are best viewed by printing them out and referring to them while using the program.
Developers, please update these notes by adding to them with each new release of the program.
Users, you can add notes at the bottom of the list, however existing notes will be locked for editing.
[6 empty] | User Note | Developer Note | Name | Date
1 | When the program loads, all toolbars except Standard and Formatting are cleared from view. Scroll is locked so that the user cannot view any cells outside the screen area. The user input screen is best viewed at a resolution of 1024x768. The zoom has not been locked, however, it is not guaranteed that all cells will be visible if the user chooses to zoom out. It is best viewed at 100%. | [6 empty] | N. Sherwood | 2006-06-27
2 | All cells are locked for editing except green marked cells. These cells are for the user to input data. | [6 empty] | N. Sherwood | 2006-06-27
Input
Output
2.1 | Cells with check boxes are automatically locked and grayed out when the check box is unchecked. To input a value, the user must first check the box. | [6 empty] | N. Sherwood | 2006-06-27
3.1 | All inputs are limited to decimal or integer values. The following is a list of restrictions placed on each input: | [6 empty] | N. Sherwood | 2009-02-27
Must be between:
| Decay constant k: | 0 |  | 0.01 | *based on normal operating procedures
| Giardia setpoint | 0 |  | 3 | *see note 4
| Virus setpoint | 0 |  | 4 | *see note 4
| Chlorine concentration | 0 |  | 5 | *based on normal operating procedures
| Temperature | 0.5 | and | 25 | *based on table values
| pH | 6.51 |  | 9 | *based on table values
| Backwash Frequency | 0 |  | 8 | *based on normal operating procedures
| Reservoir level (% Full) | 0 |  | 100
| Baffle factor | 0 |  | 1
| The program will warn the user if a value they have entered is outside these restrictions. There is no restriction on the input for flow (except that it can't be negative). | [6 empty] | N. Sherwood | 2006-06-27
3.2 | Since there are multiple inputs for pH and temperature, the program uses the minimum of each of these inputs for the calculation. For pH, the values are rounded up to the nearest integer, and for temperature, the values are rounded down to the nearest 5°C. | [6 empty] | N. Sherwood | 2006-06-27
3.3 | Top water level (TWL) of 5 m was used for the Reservoir because none was provided in drawing set. It is assumed that the bottom of the reservoir is at elevation 170.000 by averaging the variations in the slope of the reservoir floor, and the maximum TWL is 175. This was based on Drawing S401 from contract 03-10. This gives a conservative estimation of maximum reservoir volume of 13,100 m3 (CofA states that the reservoir volume is 14 ML). | [6 empty] | N. Sherwood | 2009-02-27
3.4 | Recommended baffle factor of 0.5 has been set for the Reservoir. This is based on calculations done previously at the plant, and on the volumes calculated based on the drawing set for contract 03-10. | [6 empty] | N. Sherwood | 2009-02-27
4 | Output values for log removal credits are not shown if they exceed 3 or 4-log removal respectively. This is because the disinfection tables do not provide information for CT values beyond 3 and 4-log removal. | [6 empty] | N. Sherwood | 2006-06-27
5 | Pre-filtration credits are not being considered at this time. Since GAC is used in the filters, any pre-chlorination residual will likely be 0 at the filter effluent. In addition, at the time of publication, the MOE did not permit pre-filtration to be used for disinfection credit. | [6 empty] | N. Sherwood | 2006-06-27
6.1 | It is assumed that Clearwell 1 and Clearwell 2 cannot be taken for credit. This is because the main injection points for chlorine are located downstream of the clearwells. | [6 empty] | N. Sherwood | 2009-02-27
6.2 | It is assumed that the Clearwells are run in series (CW 1, then CW 2, then UV). | [6 empty] | N. Sherwood | 2006-06-27
7 | The flow meters in the UV building are summed in the calculations for flow into the Reservoir. The sum of the flow to the distribution system is used as the flow out of the Reservoir. | [6 empty] | N. Sherwood | 2006-06-27
8 | Setting the flow to zero for any of the UV reactors means that you are shutting the valve for that reactor. Do not set all of the flow in the UV building to zero, this indicates that no flow is getting to the Reservoir, and that no flow is leaving the Clearwells. The plant cannot run for long in this configuration, as the Reservoir will empty, and the Clearwells will overflow. | [6 empty] | N. Sherwood | 2006-06-27
8.1 | UV disinfection is based on the lowest dosage (in mJ/cm2) of the UV reactors. Therefore, by setting one of the dosages to zero, it is the same as turning off all the reactors (but not the flow). However, if the flow is set to zero for any of the UV reactors, the adjoining dose no longer affects the calculation. | [6 empty] | N. Sherwood | 2006-06-27
8.2 | UV credit is applied separate from the Disinfection Credits. The current C of A for the plant states: "an Ultraviolet Primary Disinfection System consisting of five (5) UV reactors (four duty, one standby) installed downstream of the existing clearwells in a new UV disinfection Building, designed to provide a minimum disinfection dose of 40 mJ/cm2 at 254 nm at the end of lamp life and at a UV transmittance of 90% for the maximum flow rate of 1736 L/s (150 ML/d) and provide a minimum 3-log inactivation of Giardia." So if the CT Calculator detects a dosage below 40 mJ/cm2, no credit will be applied, and the cells will turn red. | [6 empty] | N. Sherwood | 2009-02-27
9 | A Safety Factor has been included for each distribution point to provide the operator with a representation of the realtime factor of safety that is being implemented at current measurements of pH, temperature, flow, and chlorine residual. The Safety Factor will turn red (alarm) when it drops below 1.2. A Safety Factor of less than 1 means the plant is running out of compliance. | [6 empty] | N. Sherwood | 2006-06-27
10 | A Filtration Credit can been applied for use in calculating total reduction of Giardia and Viruses. In order to be considered conventional filtration and claim the 2.5 log Giardia cyst removal and 2 log virus removal credit, the filtration process must meet the following criteria: * use a chemical coagulant at all times when the treatment plant is in operation; * monitor and adjust chemical dosages in response to variations in raw water quality; * maintain effective backwash procedures, including filter-to-waste or an equivalent procedure during filter ripening to ensure that the effluent turbidity requirements are met at all times; * continuously monitor filtrate turbidity from each filter; and * meet the performance criterion for filtered water turbidity of less than or equal to 0.3 NTU in 95% of the measurements each month. | [6 empty] | N. Sherwood | 2006-06-27
10.1 | If the filters are meeting the above requirements, then the warning setpoint for Chlorine Credits should be 0.5-log for Giardia and 2-log for Virus in order to meet the treatment requirement of 3-log Giardia and 4-log Virus. | [6 empty] | N. Sherwood | 2009-02-27
13.1 | Backwash water is taken from Clearwell 2. This is subtracted as a volume per backwash. The volume is based on the filter narrative which states that 214 m3 of water is needed per backwash cycle, per filter. The narrative also states that the filters are always backwashed in pairs. This is why the input for the number of filters is in pairs of filters. This input will affect the 1-hour forecast values, as the volume in the Reservoir(s) will have dropped based on the amount of backwashing required. | [6 empty] | N. Sherwood | 2006-06-27
13.2 | Because of possible short circuiting, the high lift pump wells have not been counted any credit. | [6 empty] | N. Sherwood | 2006-06-27
14.1 | There is an estimated 83 m of pipe between the UV Building and the Reservoir. | [6 empty] | N. Sherwood | 2006-06-27
14.2 | There is an estimated 180 m of pipe between the Reservoir and the High Lift Pumps. | [6 empty] | N. Sherwood | 2006-06-27
15.1 | The log removal credit has been calculated using a combination of the integrated form of the decay equation, and the Chick-Watson model. By integrating this combination, the result is an equation relating log-removal to decay constant k, initial concentration Co, baffle factor x, and hydraulic detention time, td. | [6 empty] | N. Sherwood | 2006-06-27
15.2 | The CT disinfection tables supplied by the Ministry of the Environment (Procedure for Disinfection of Drinking Water in Ontario) have been digitized so that log-removals can be calculated for each pH, temperature and concentration. | [6 empty] | N. Sherwood | 2006-06-27
15.3 | The decay constant k can be calculated by using the measured residual concentrations before and after the reservoirs, and dividing by hydraulic detention time. This decay constant can also be included as a measured value (i.e. using post filtration water and testing decay in the lab). To clarify: the calculated k is an output from the program based on inputs such as chlorine residual and flow, and the measured k is an input that the user specifies based on laboratory results. | [6 empty] | N. Sherwood | 2006-06-27
15.4 | It is recommended that the calculated k be field verified using a bench scale test. If results are shown to vary significantly from the calculated k, it is recommended that a measured k be used. | [6 empty] | N. Sherwood | 2006-06-27
99.1 | Version 1.1 changes made to match PLC CT calculator provided for Region. Changes are dated 2/27/2009. | [6 empty] | N. Sherwood | 2009-02-27

## Calculations (hidden)
Segment | Description | Volume | Flow | HDT | Baffle | T10 | pH | round | Co | round | Temp | round | Giardia | Log | Log |  | Virus | Log | Log
|  | m3 | L/s | min |  | min |  | up | mg/L | up | °C | down | k | eqn 1 | eqn 2 | max | k | eqn 1 | eqn 2 | max
1 | River Intake Pipe
2 | Raw Water Well
3
21
22 | Pipe to Clearwell |  | 0 |  | 1
23 | Clearwell | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | #VALUE! | #VALUE! | 0 | #VALUE! | 0 | 0 | 0 | 0
24 | Pipe CW to Tower | 23.5619 | 0 | #DIV/0! | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0.5 | #VALUE! | #VALUE! | 0 | #VALUE! | 0 | #DIV/0! | 0 | #DIV/0!
25 | Tower | 300 | 0 | #DIV/0! | 0.1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0.5 | #VALUE! | #VALUE! | 0 | #VALUE! | 0 | #DIV/0! | 0 | #DIV/0!
26 | Pipe Tower to 1st User |  | 0 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | #VALUE! |  |  | 0 | 0 |  |  | 0
1-Hour Forecast
| Clearwell | 0 | 0 | 0 | 0.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0.5 | #VALUE! | #VALUE! | 0 | #VALUE! | 0 | 0 | 0 | 0
24 | Pipe CW to Tower | 23.5619 | 0 | #DIV/0! | 1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0.5 | #VALUE! | #VALUE! | 0 | #VALUE! | 0 | #DIV/0! | 0 | #DIV/0!
| Tower | 300 | 0 | #DIV/0! | 0.1 | #DIV/0! | 0 | 0 | 0 | 0 | 0 | 0.5 | #VALUE! | #VALUE! | 0 | #VALUE! | 0 | #DIV/0! | 0 | #DIV/0!
Summary of Inactivation Credits
|  | Log Inactivation |  |  | Volumes
| Component | Giardia | Virsuses |  | Clearwell |  |  | 100 |  |  |  | Log Eqn 2 Formulas:
| Chlorine | #VALUE! | #DIV/0! |  | Pipe from CW to Tower |  |  | 23.5619 |  |  |  | Giardia | Log-reduction = CT Actual / [0.2828 x (pH)^2.69 x (Free Cl Conc.)^0.15 x 0.933^(Temp. - 5)]
| 4 Hr Forecast (Cl Only) | #VALUE! | #DIV/0! |  | Tower |  |  | 1000 |  |  |  | Viruses | Log-reduction = {[CT Actual x e^(0.071 x Temp.)] - 0.42} / 2.94
| CT Achieved | #DIV/0! | #DIV/0!
| CT Required | #DIV/0! | #DIV/0!
Note on J1: Nathan Sherwood: These concentrations are at the beginning of each section. This is in order to calculate the log inactivation based on the formula derived (integrated method).
Note on N1: nsherwood: this is a "constant" in the log-inact. formula, which is based on the current temperature. By using concentration and pH, these cells use the lookup function to get the appropriate k from the "Giardia CT" sheet
Note on O1: nsherwood: This log-inactivation formula uses the appropriate values in the adjacent cells to calculate the log-reduction for a particular segment

## Giardia CT (hidden)
CT Tables | [6 empty] | Giardia Cysts | [9 empty] | Temperature 1: | 0.5 | oC
[7 empty] | Average K values for every temp, pH | [9 empty] | Giardia k Table | pH
Giardia Cysts | [6 empty] | Cf | k | Cf | k | Cf | k | Cf | k | Cf | k | Co | 7 | 7.5 | 8 | 8.5 | 9
Temp | pH | Free Cl2 Conc | log inactivation | CT | k | temp: |  | 0.5 |  | 5 |  | 10 |  | 15 |  | 20 | 0 | 0 | 0 | 0 | 0 | 0
0.5 | 7 | 0.4 | 0.5 | 33 | 0.015152 | pH: |  | 7 |  | 7 |  | 7 |  | 7 |  | 7 | 0.4 | 0.015325 | 0.012618 | 0.010832 | 0.009108 | 0.0076923 | 3
0.5 | 7 | 0.4 | 1 | 65 | 0.015385 |  | 0.4 | 0.015325 | 0.4 | 0.021591 | 0.4 | 0.028899 | 0.4 | 0.042753 | 0.4 | 0.057508 | 0.6 | 0.015014 | 0.012532 | 0.010483 | 0.0087719 | 0.0073641 | 4
0.5 | 7 | 0.4 | 1.5 | 98 | 0.015306 |  | 0.6 | 0.015014 | 0.6 | 0.020923 | 0.6 | 0.027918 | 0.6 | 0.041667 | 0.6 | 0.055556 | 0.8 | 0.014638 | 0.012195 | 0.010171 | 0.0084746 | 0.0071121 | 5
0.5 | 7 | 0.4 | 2 | 130 | 0.015385 |  | 0.8 | 0.014638 | 0.8 | 0.020575 | 0.8 | 0.02732 | 0.8 | 0.041128 | 0.8 | 0.054605 | 1 | 0.014286 | 0.01186 | 0.0098626 | 0.0082106 | 0.006859 | 6
0.5 | 7 | 0.4 | 2.5 | 163 | 0.015337 |  | 1 | 0.014286 | 1 | 0.020083 | 1 | 0.026744 | 1 | 0.039603 | 1 | 0.053763 | 1.2 | 0.013929 | 0.011585 | 0.0095862 | 0.0079749 | 0.0066526 | 7
0.5 | 7 | 0.4 | 3 | 195 | 0.015385 |  | 1.2 | 0.013929 | 1.2 | 0.019761 | 1.2 | 0.026316 | 1.2 | 0.039385 | 1.2 | 0.05195 | 1.4 | 0.013776 | 0.011286 | 0.0093236 | 0.0077367 | 0.0064681 | 8
0.5 | 7 | 0.6 | 0.5 | 33 | 0.015152 |  | 1.4 | 0.013776 | 1.4 | 0.019307 | 1.4 | 0.025905 | 1.4 | 0.038462 | 1.4 | 0.051574 | 1.6 | 0.013264 | 0.010958 | 0.009108 | 0.0075577 | 0.0062792 | 9
0.5 | 7 | 0.6 | 1 | 67 | 0.014925 |  | 1.6 | 0.013264 | 1.6 | 0.01901 | 1.6 | 0.02513 | 1.6 | 0.038002 | 1.6 | 0.050525 | 1.8 | 0.012944 | 0.010723 | 0.0088806 | 0.0073641 | 0.0061254 | 10
0.5 | 7 | 0.6 | 1.5 | 100 | 0.015 |  | 1.8 | 0.012944 | 1.8 | 0.018519 | 1.8 | 0.024629 | 1.8 | 0.036696 | 1.8 | 0.049228 | 2 | 0.012722 | 0.010483 | 0.008666 | 0.0071811 | 0.0060022 | 11
0.5 | 7 | 0.6 | 2 | 133 | 0.015038 |  | 2 | 0.012722 | 2 | 0.018098 | 2 | 0.024159 | 2 | 0.03598 | 2 | 0.048542 | 2.2 | 0.012406 | 0.010075 | 0.0084894 | 0.0070423 | 0.0058714 | 12
0.5 | 7 | 0.6 | 2.5 | 167 | 0.01497 |  | 2.2 | 0.012406 | 2.2 | 0.017757 | 2.2 | 0.023632 | 2.2 | 0.035318 | 2.2 | 0.047059 | 2.4 | 0.012148 | 0.010061 | 0.0083114 | 0.0068845 | 0.0057471 | 13
0.5 | 7 | 0.6 | 3 | 200 | 0.015 |  | 2.4 | 0.012148 | 2.4 | 0.017424 | 2.4 | 0.02312 | 2.4 | 0.034962 | 2.4 | 0.045888 | 2.6 | 0.011905 | 0.0098626 | 0.0081563 | 0.0067568 | 0.0056245 | 14
0.5 | 7 | 0.8 | 0.5 | 34 | 0.014706 |  | 2.6 | 0.011905 | 2.6 | 0.017148 | 2.6 | 0.022834 | 2.6 | 0.034024 | 2.6 | 0.045455 | 2.8 | 0.011656 | 0.0096718 | 0.0079837 | 0.0066399 | 0.0055171 | 15
0.5 | 7 | 0.8 | 1 | 68 | 0.014706 |  | 2.8 | 0.011656 | 2.8 | 0.016837 | 2.8 | 0.02242 | 2.8 | 0.033565 | 2.8 | 0.044815 | 3 | 0.011461 | 0.0094882 | 0.0078497 | 0.0065192 | 0.0054348 | 16
0.5 | 7 | 0.8 | 1.5 | 103 | 0.014563 |  | 3 | 0.011461 | 3 | 0.016501 | 3 | 0.021837 | 3 | 0.032987 | 3 | 0.044245
0.5 | 7 | 0.8 | 2 | 137 | 0.014599 | temp: |  | 0.5 |  | 5 |  | 10 |  | 15 |  | 20
0.5 | 7 | 0.8 | 2.5 | 171 | 0.01462 | pH: |  | 7.5 |  | 7.5 |  | 7.5 |  | 7.5 |  | 7.5
0.5 | 7 | 0.8 | 3 | 205 | 0.014634 |  | 0.4 | 0.012618 | 0.4 | 0.018053 | 0.4 | 0.023927 | 0.4 | 0.03598 | 0.4 | 0.048542
0.5 | 7 | 1 | 0.5 | 35 | 0.014286 |  | 0.6 | 0.012532 | 0.6 | 0.017466 | 0.6 | 0.023472 | 0.6 | 0.034962 | 0.6 | 0.046751
0.5 | 7 | 1 | 1 | 70 | 0.014286 |  | 0.8 | 0.012195 | 0.8 | 0.017148 | 0.8 | 0.022834 | 0.8 | 0.034024 | 0.8 | 0.045455
0.5 | 7 | 1 | 1.5 | 105 | 0.014286 |  | 1 | 0.01186 | 1 | 0.016724 | 1 | 0.02242 | 1 | 0.033333 | 1 | 0.044815
0.5 | 7 | 1 | 2 | 140 | 0.014286 |  | 1.2 | 0.011585 | 1.2 | 0.016326 | 1.2 | 0.021837 | 1.2 | 0.032677 | 1.2 | 0.04301
0.5 | 7 | 1 | 2.5 | 175 | 0.014286 |  | 1.4 | 0.011286 | 1.4 | 0.016047 | 1.4 | 0.021458 | 1.4 | 0.031856 | 1.4 | 0.042753
0.5 | 7 | 1 | 3 | 210 | 0.014286 |  | 1.6 | 0.010958 | 1.6 | 0.015625 | 1.6 | 0.020833 | 1.6 | 0.03125 | 1.6 | 0.041667
0.5 | 7 | 1.2 | 0.5 | 36 | 0.013889 |  | 1.8 | 0.010723 | 1.8 | 0.015292 | 1.8 | 0.020303 | 1.8 | 0.030672 | 1.8 | 0.040648
0.5 | 7 | 1.2 | 1 | 72 | 0.013889 |  | 2 | 0.010483 | 2 | 0.015014 | 2 | 0.02 | 2 | 0.029948 | 2 | 0.039603
0.5 | 7 | 1.2 | 1.5 | 108 | 0.013889 |  | 2.2 | 0.010075 | 2.2 | 0.014706 | 2.2 | 0.019511 | 2.2 | 0.029412 | 2.2 | 0.038771
0.5 | 7 | 1.2 | 2 | 143 | 0.013986 |  | 2.4 | 0.010061 | 2.4 | 0.014328 | 2.4 | 0.019115 | 2.4 | 0.028367 | 2.4 | 0.038462
0.5 | 7 | 1.2 | 2.5 | 179 | 0.013966 |  | 2.6 | 0.0098626 | 2.6 | 0.014034 | 2.6 | 0.018729 | 2.6 | 0.027938 | 2.6 | 0.037591
0.5 | 7 | 1.2 | 3 | 215 | 0.013953 |  | 2.8 | 0.0096718 | 2.8 | 0.013828 | 2.8 | 0.018411 | 2.8 | 0.027537 | 2.8 | 0.036696
0.5 | 7 | 1.4 | 0.5 | 37 | 0.013514 |  | 3 | 0.0094882 | 3 | 0.013551 | 3 | 0.018053 | 3 | 0.026844 | 3 | 0.03598
0.5 | 7 | 1.4 | 1 | 74 | 0.013514 | temp: |  | 0.5 |  | 5 |  | 10 |  | 15 |  | 20
0.5 | 7 | 1.4 | 1.5 | 111 | 0.013514 | pH: |  | 8 |  | 8 |  | 8 |  | 8 |  | 8
0.5 | 7 | 1.4 | 2 | 147 | 0.013605 |  | 0.4 | 0.010832 | 0.4 | 0.015152 | 0.4 | 0.020083 | 0.4 | 0.030074 | 0.4 | 0.040648
0.5 | 7 | 1.4 | 2.5 | 184 | 0.013587 |  | 0.6 | 0.010483 | 0.6 | 0.014706 | 0.6 | 0.019511 | 0.6 | 0.029412 | 0.6 | 0.038771
0.5 | 7 | 1.4 | 3 | 201 | 0.014925 |  | 0.8 | 0.010171 | 0.8 | 0.014286 | 0.8 | 0.01901 | 0.8 | 0.028367 | 0.8 | 0.038002
0.5 | 7 | 1.6 | 0.5 | 38 | 0.013158 |  | 1 | 0.0098626 | 1 | 0.013889 | 1 | 0.018519 | 1 | 0.027778 | 1 | 0.036696
0.5 | 7 | 1.6 | 1 | 75 | 0.013333 |  | 1.2 | 0.0095862 | 1.2 | 0.013551 | 1.2 | 0.018053 | 1.2 | 0.026766 | 1.2 | 0.03598
0.5 | 7 | 1.6 | 1.5 | 113 | 0.013274 |  | 1.4 | 0.0093236 | 1.4 | 0.013194 | 1.4 | 0.017667 | 1.4 | 0.026316 | 1.4 | 0.035318
0.5 | 7 | 1.6 | 2 | 151 | 0.013245 |  | 1.6 | 0.009108 | 1.6 | 0.012921 | 1.6 | 0.017241 | 1.6 | 0.025905 | 1.6 | 0.034187
0.5 | 7 | 1.6 | 2.5 | 188 | 0.013298 |  | 1.8 | 0.0088806 | 1.8 | 0.012596 | 1.8 | 0.016724 | 1.8 | 0.02513 | 1.8 | 0.033565
0.5 | 7 | 1.6 | 3 | 226 | 0.013274 |  | 2 | 0.008666 | 2 | 0.012307 | 2 | 0.016501 | 2 | 0.024629 | 2 | 0.032987
0.5 | 7 | 1.8 | 0.5 | 39 | 0.012821 |  | 2.2 | 0.0084894 | 2.2 | 0.012106 | 2.2 | 0.016129 | 2.2 | 0.024159 | 2.2 | 0.031998
0.5 | 7 | 1.8 | 1 | 77 | 0.012987 |  | 2.4 | 0.0083114 | 2.4 | 0.01186 | 2.4 | 0.015775 | 2.4 | 0.023632 | 2.4 | 0.031453
0.5 | 7 | 1.8 | 1.5 | 116 | 0.012931 |  | 2.6 | 0.0081563 | 2.6 | 0.011628 | 2.6 | 0.015479 | 2.6 | 0.02312 | 2.6 | 0.030946
0.5 | 7 | 1.8 | 2 | 154 | 0.012987 |  | 2.8 | 0.0079837 | 2.8 | 0.01139 | 2.8 | 0.015199 | 2.8 | 0.022727 | 2.8 | 0.030074
0.5 | 7 | 1.8 | 2.5 | 193 | 0.012953 |  | 3 | 0.0078497 | 3 | 0.011187 | 3 | 0.014869 | 3 | 0.02242 | 3 | 0.029592
0.5 | 7 | 1.8 | 3 | 231 | 0.012987 | temp: |  | 0.5 |  | 5 |  | 10 |  | 15 |  | 20
0.5 | 7 | 2 | 0.5 | 39 | 0.012821 | pH: |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5 |  | 8.5
0.5 | 7 | 2 | 1 | 79 | 0.012658 |  | 0.4 | 0.009108 | 0.4 | 0.012722 | 0.4 | 0.016877 | 0.4 | 0.025386 | 0.4 | 0.033565
0.5 | 7 | 2 | 1.5 | 118 | 0.012712 |  | 0.6 | 0.0087719 | 0.6 | 0.012286 | 0.6 | 0.016326 | 0.6 | 0.024629 | 0.6 | 0.032677
0.5 | 7 | 2 | 2 | 157 | 0.012739 |  | 0.8 | 0.0084746 | 0.8 | 0.011905 | 0.8 | 0.015809 | 0.8 | 0.02381 | 0.8 | 0.031453
0.5 | 7 | 2 | 2.5 | 197 | 0.01269 |  | 1 | 0.0082106 | 1 | 0.011547 | 1 | 0.015325 | 1 | 0.023046 | 1 | 0.030672
0.5 | 7 | 2 | 3 | 236 | 0.012712 |  | 1.2 | 0.0079749 | 1.2 | 0.011204 | 1.2 | 0.015014 | 1.2 | 0.02242 | 1.2 | 0.029948
0.5 | 7 | 2.2 | 0.5 | 40 | 0.0125 |  | 1.4 | 0.0077367 | 1.4 | 0.010942 | 1.4 | 0.014576 | 1.4 | 0.021837 | 1.4 | 0.029142
0.5 | 7 | 2.2 | 1 | 81 | 0.012346 |  | 1.6 | 0.0075577 | 1.6 | 0.010662 | 1.6 | 0.014222 | 1.6 | 0.021163 | 1.6 | 0.028367
0.5 | 7 | 2.2 | 1.5 | 121 | 0.012397 |  | 1.8 | 0.0073641 | 1.8 | 0.010439 | 1.8 | 0.013929 | 1.8 | 0.020945 | 1.8 | 0.027778
0.5 | 7 | 2.2 | 2 | 161 | 0.012422 |  | 2 | 0.0071811 | 2 | 0.010204 | 2 | 0.013551 | 2 | 0.020303 | 2 | 0.02732
0.5 | 7 | 2.2 | 2.5 | 202 | 0.012376 |  | 2.2 | 0.0070423 | 2.2 | 0.01 | 2.2 | 0.013288 | 2.2 | 0.02 | 2.2 | 0.02646
0.5 | 7 | 2.2 | 3 | 242 | 0.012397 |  | 2.4 | 0.0068845 | 2.4 | 0.0098039 | 2.4 | 0.013054 | 2.4 | 0.019511 | 2.4 | 0.02555
0.5 | 7 | 2.4 | 0.5 | 41 | 0.012195 |  | 2.6 | 0.0067568 | 2.6 | 0.0096154 | 2.6 | 0.012821 | 2.6 | 0.019231 | 2.6 | 0.025476
0.5 | 7 | 2.4 | 1 | 82 | 0.012195 |  | 2.8 | 0.0066399 | 2.8 | 0.009434 | 2.8 | 0.012532 | 2.8 | 0.018778 | 2.8 | 0.02513
0.5 | 7 | 2.4 | 1.5 | 124 | 0.012097 |  | 3 | 0.0065192 | 3 | 0.0092593 | 3 | 0.012307 | 3 | 0.018519 | 3 | 0.024629
0.5 | 7 | 2.4 | 2 | 165 | 0.012121 | temp: |  | 0.5 |  | 5 |  | 10 |  | 15 |  | 20
0.5 | 7 | 2.4 | 2.5 | 206 | 0.012136 | pH: |  | 9 |  | 9 |  | 9 |  | 9 |  | 9
0.5 | 7 | 2.4 | 3 | 247 | 0.012146 |  | 0.4 | 0.0076923 | 0.4 | 0.010723 | 0.4 | 0.014328 | 0.4 | 0.021458 | 0.4 | 0.028367
0.5 | 7 | 2.6 | 0.5 | 42 | 0.011905 |  | 0.6 | 0.0073641 | 0.6 | 0.010282 | 0.6 | 0.013773 | 0.6 | 0.020575 | 0.6 | 0.027537
0.5 | 7 | 2.6 | 1 | 84 | 0.011905 |  | 0.8 | 0.0071121 | 0.8 | 0.0099685 | 0.8 | 0.013264 | 0.8 | 0.019875 | 0.8 | 0.02646
0.5 | 7 | 2.6 | 1.5 | 126 | 0.011905 |  | 1 | 0.006859 | 1 | 0.0096154 | 1 | 0.012821 | 1 | 0.019231 | 1 | 0.025476
0.5 | 7 | 2.6 | 2 | 168 | 0.011905 |  | 1.2 | 0.0066526 | 1.2 | 0.0093805 | 1.2 | 0.0125 | 1.2 | 0.018729 | 1.2 | 0.025
0.5 | 7 | 2.6 | 2.5 | 210 | 0.011905 |  | 1.4 | 0.0064681 | 1.4 | 0.009108 | 1.4 | 0.012148 | 1.4 | 0.018098 | 1.4 | 0.024241
0.5 | 7 | 2.6 | 3 | 252 | 0.011905 |  | 1.6 | 0.0062792 | 1.6 | 0.0089034 | 1.6 | 0.01186 | 1.6 | 0.017757 | 1.6 | 0.02381
0.5 | 7 | 2.8 | 0.5 | 43 | 0.011628 |  | 1.8 | 0.0061254 | 1.8 | 0.0086765 | 1.8 | 0.011585 | 1.8 | 0.017303 | 1.8 | 0.02312
0.5 | 7 | 2.8 | 1 | 86 | 0.011628 |  | 2 | 0.0060022 | 2 | 0.0084894 | 2 | 0.011323 | 2 | 0.016877 | 2 | 0.022727
0.5 | 7 | 2.8 | 1.5 | 129 | 0.011628 |  | 2.2 | 0.0058714 | 2.2 | 0.0083114 | 2.2 | 0.011072 | 2.2 | 0.016579 | 2.2 | 0.022098
0.5 | 7 | 2.8 | 2 | 171 | 0.011696 |  | 2.4 | 0.0057471 | 2.4 | 0.0081563 | 2.4 | 0.01087 | 2.4 | 0.016289 | 2.4 | 0.021739
0.5 | 7 | 2.8 | 2.5 | 214 | 0.011682 |  | 2.6 | 0.0056245 | 2.6 | 0.0079837 | 2.6 | 0.010662 | 2.6 | 0.015973 | 2.6 | 0.021163
0.5 | 7 | 2.8 | 3 | 257 | 0.011673 |  | 2.8 | 0.0055171 | 2.8 | 0.0078497 | 2.8 | 0.010439 | 2.8 | 0.015676 | 2.8 | 0.020923
0.5 | 7 | 3 | 0.5 | 44 | 0.011364 |  | 3 | 0.0054348 | 3 | 0.0077045 | 3 | 0.010268 | 3 | 0.015325 | 3 | 0.020575
0.5 | 7 | 3 | 1 | 87 | 0.011494
0.5 | 7 | 3 | 1.5 | 131 | 0.01145
0.5 | 7 | 3 | 2 | 174 | 0.011494
0.5 | 7 | 3 | 2.5 | 218 | 0.011468
0.5 | 7 | 3 | 3 | 261 | 0.011494
0.5 | 7.5 | 0.4 | 0.5 | 40 | 0.0125
0.5 | 7.5 | 0.4 | 1 | 79 | 0.012658
0.5 | 7.5 | 0.4 | 1.5 | 119 | 0.012605
0.5 | 7.5 | 0.4 | 2 | 158 | 0.012658
0.5 | 7.5 | 0.4 | 2.5 | 198 | 0.012626
0.5 | 7.5 | 0.4 | 3 | 237 | 0.012658
0.5 | 7.5 | 0.6 | 0.5 | 40 | 0.0125
0.5 | 7.5 | 0.6 | 1 | 80 | 0.0125
0.5 | 7.5 | 0.6 | 1.5 | 120 | 0.0125
0.5 | 7.5 | 0.6 | 2 | 159 | 0.012579
0.5 | 7.5 | 0.6 | 2.5 | 199 | 0.012563
0.5 | 7.5 | 0.6 | 3 | 239 | 0.012552
0.5 | 7.5 | 0.8 | 0.5 | 41 | 0.012195
0.5 | 7.5 | 0.8 | 1 | 82 | 0.012195
0.5 | 7.5 | 0.8 | 1.5 | 123 | 0.012195
0.5 | 7.5 | 0.8 | 2 | 164 | 0.012195
0.5 | 7.5 | 0.8 | 2.5 | 205 | 0.012195
0.5 | 7.5 | 0.8 | 3 | 246 | 0.012195
0.5 | 7.5 | 1 | 0.5 | 42 | 0.011905
0.5 | 7.5 | 1 | 1 | 84 | 0.011905
0.5 | 7.5 | 1 | 1.5 | 127 | 0.011811
0.5 | 7.5 | 1 | 2 | 169 | 0.011834
0.5 | 7.5 | 1 | 2.5 | 211 | 0.011848
0.5 | 7.5 | 1 | 3 | 253 | 0.011858
0.5 | 7.5 | 1.2 | 0.5 | 43 | 0.011628
0.5 | 7.5 | 1.2 | 1 | 86 | 0.011628
0.5 | 7.5 | 1.2 | 1.5 | 130 | 0.011538
0.5 | 7.5 | 1.2 | 2 | 173 | 0.011561
0.5 | 7.5 | 1.2 | 2.5 | 216 | 0.011574
0.5 | 7.5 | 1.2 | 3 | 259 | 0.011583
0.5 | 7.5 | 1.4 | 0.5 | 44 | 0.011364
0.5 | 7.5 | 1.4 | 1 | 89 | 0.011236
0.5 | 7.5 | 1.4 | 1.5 | 133 | 0.011278
0.5 | 7.5 | 1.4 | 2 | 177 | 0.011299
0.5 | 7.5 | 1.4 | 2.5 | 222 | 0.011261
0.5 | 7.5 | 1.4 | 3 | 266 | 0.011278
0.5 | 7.5 | 1.6 | 0.5 | 46 | 0.01087
0.5 | 7.5 | 1.6 | 1 | 91 | 0.010989
0.5 | 7.5 | 1.6 | 1.5 | 137 | 0.010949
0.5 | 7.5 | 1.6 | 2 | 182 | 0.010989
0.5 | 7.5 | 1.6 | 2.5 | 228 | 0.010965
0.5 | 7.5 | 1.6 | 3 | 273 | 0.010989
0.5 | 7.5 | 1.8 | 0.5 | 47 | 0.010638
0.5 | 7.5 | 1.8 | 1 | 93 | 0.010753
0.5 | 7.5 | 1.8 | 1.5 | 140 | 0.010714
0.5 | 7.5 | 1.8 | 2 | 186 | 0.010753
0.5 | 7.5 | 1.8 | 2.5 | 233 | 0.01073
0.5 | 7.5 | 1.8 | 3 | 279 | 0.010753
0.5 | 7.5 | 2 | 0.5 | 48 | 0.010417
0.5 | 7.5 | 2 | 1 | 95 | 0.010526
0.5 | 7.5 | 2 | 1.5 | 143 | 0.01049
0.5 | 7.5 | 2 | 2 | 191 | 0.010471
0.5 | 7.5 | 2 | 2.5 | 238 | 0.010504
0.5 | 7.5 | 2 | 3 | 286 | 0.01049
0.5 | 7.5 | 2.2 | 0.5 | 50 | 0.01
0.5 | 7.5 | 2.2 | 1 | 99 | 0.010101
0.5 | 7.5 | 2.2 | 1.5 | 149 | 0.010067
0.5 | 7.5 | 2.2 | 2 | 198 | 0.010101
0.5 | 7.5 | 2.2 | 2.5 | 248 | 0.010081
0.5 | 7.5 | 2.2 | 3 | 297 | 0.010101
0.5 | 7.5 | 2.4 | 0.5 | 50 | 0.01
0.5 | 7.5 | 2.4 | 1 | 99 | 0.010101
0.5 | 7.5 | 2.4 | 1.5 | 149 | 0.010067
0.5 | 7.5 | 2.4 | 2 | 199 | 0.01005
0.5 | 7.5 | 2.4 | 2.5 | 248 | 0.010081
0.5 | 7.5 | 2.4 | 3 | 298 | 0.010067
0.5 | 7.5 | 2.6 | 0.5 | 51 | 0.0098039
0.5 | 7.5 | 2.6 | 1 | 101 | 0.009901
0.5 | 7.5 | 2.6 | 1.5 | 152 | 0.0098684
0.5 | 7.5 | 2.6 | 2 | 203 | 0.0098522
0.5 | 7.5 | 2.6 | 2.5 | 253 | 0.0098814
0.5 | 7.5 | 2.6 | 3 | 304 | 0.0098684
0.5 | 7.5 | 2.8 | 0.5 | 52 | 0.0096154
0.5 | 7.5 | 2.8 | 1 | 103 | 0.0097087
0.5 | 7.5 | 2.8 | 1.5 | 155 | 0.0096774
0.5 | 7.5 | 2.8 | 2 | 207 | 0.0096618
0.5 | 7.5 | 2.8 | 2.5 | 258 | 0.0096899
0.5 | 7.5 | 2.8 | 3 | 310 | 0.0096774
0.5 | 7.5 | 3 | 0.5 | 53 | 0.009434
0.5 | 7.5 | 3 | 1 | 105 | 0.0095238
0.5 | 7.5 | 3 | 1.5 | 158 | 0.0094937
0.5 | 7.5 | 3 | 2 | 211 | 0.0094787
0.5 | 7.5 | 3 | 2.5 | 263 | 0.0095057
0.5 | 7.5 | 3 | 3 | 316 | 0.0094937
0.5 | 8 | 0.4 | 0.5 | 46 | 0.01087
0.5 | 8 | 0.4 | 1 | 92 | 0.01087
0.5 | 8 | 0.4 | 1.5 | 139 | 0.010791
0.5 | 8 | 0.4 | 2 | 185 | 0.010811
0.5 | 8 | 0.4 | 2.5 | 231 | 0.010823
0.5 | 8 | 0.4 | 3 | 277 | 0.01083
0.5 | 8 | 0.6 | 0.5 | 48 | 0.010417
0.5 | 8 | 0.6 | 1 | 95 | 0.010526
0.5 | 8 | 0.6 | 1.5 | 143 | 0.01049
0.5 | 8 | 0.6 | 2 | 191 | 0.010471
0.5 | 8 | 0.6 | 2.5 | 238 | 0.010504
0.5 | 8 | 0.6 | 3 | 286 | 0.01049
0.5 | 8 | 0.8 | 0.5 | 49 | 0.010204
0.5 | 8 | 0.8 | 1 | 98 | 0.010204
0.5 | 8 | 0.8 | 1.5 | 148 | 0.010135
0.5 | 8 | 0.8 | 2 | 197 | 0.010152
0.5 | 8 | 0.8 | 2.5 | 246 | 0.010163
0.5 | 8 | 0.8 | 3 | 295 | 0.010169
0.5 | 8 | 1 | 0.5 | 51 | 0.0098039
0.5 | 8 | 1 | 1 | 101 | 0.009901
0.5 | 8 | 1 | 1.5 | 152 | 0.0098684
0.5 | 8 | 1 | 2 | 203 | 0.0098522
0.5 | 8 | 1 | 2.5 | 253 | 0.0098814
0.5 | 8 | 1 | 3 | 304 | 0.0098684
0.5 | 8 | 1.2 | 0.5 | 52 | 0.0096154
0.5 | 8 | 1.2 | 1 | 104 | 0.0096154
0.5 | 8 | 1.2 | 1.5 | 157 | 0.0095541
0.5 | 8 | 1.2 | 2 | 209 | 0.0095694
0.5 | 8 | 1.2 | 2.5 | 261 | 0.0095785
0.5 | 8 | 1.2 | 3 | 313 | 0.0095847
0.5 | 8 | 1.4 | 0.5 | 54 | 0.0092593
0.5 | 8 | 1.4 | 1 | 107 | 0.0093458
0.5 | 8 | 1.4 | 1.5 | 161 | 0.0093168
0.5 | 8 | 1.4 | 2 | 214 | 0.0093458
0.5 | 8 | 1.4 | 2.5 | 268 | 0.0093284
0.5 | 8 | 1.4 | 3 | 321 | 0.0093458
0.5 | 8 | 1.6 | 0.5 | 55 | 0.0090909
0.5 | 8 | 1.6 | 1 | 110 | 0.0090909
0.5 | 8 | 1.6 | 1.5 | 165 | 0.0090909
0.5 | 8 | 1.6 | 2 | 219 | 0.0091324
0.5 | 8 | 1.6 | 2.5 | 274 | 0.0091241
0.5 | 8 | 1.6 | 3 | 329 | 0.0091185
0.5 | 8 | 1.8 | 0.5 | 56 | 0.0089286
0.5 | 8 | 1.8 | 1 | 113 | 0.0088496
0.5 | 8 | 1.8 | 1.5 | 169 | 0.0088757
0.5 | 8 | 1.8 | 2 | 225 | 0.0088889
0.5 | 8 | 1.8 | 2.5 | 282 | 0.0088652
0.5 | 8 | 1.8 | 3 | 338 | 0.0088757
0.5 | 8 | 2 | 0.5 | 58 | 0.0086207
0.5 | 8 | 2 | 1 | 115 | 0.0086957
0.5 | 8 | 2 | 1.5 | 173 | 0.0086705
0.5 | 8 | 2 | 2 | 231 | 0.008658
0.5 | 8 | 2 | 2.5 | 288 | 0.0086806
0.5 | 8 | 2 | 3 | 346 | 0.0086705
0.5 | 8 | 2.2 | 0.5 | 59 | 0.0084746
0.5 | 8 | 2.2 | 1 | 118 | 0.0084746
0.5 | 8 | 2.2 | 1.5 | 177 | 0.0084746
0.5 | 8 | 2.2 | 2 | 235 | 0.0085106
0.5 | 8 | 2.2 | 2.5 | 294 | 0.0085034
0.5 | 8 | 2.2 | 3 | 353 | 0.0084986
0.5 | 8 | 2.4 | 0.5 | 60 | 0.0083333
0.5 | 8 | 2.4 | 1 | 120 | 0.0083333
0.5 | 8 | 2.4 | 1.5 | 181 | 0.0082873
0.5 | 8 | 2.4 | 2 | 241 | 0.0082988
0.5 | 8 | 2.4 | 2.5 | 301 | 0.0083056
0.5 | 8 | 2.4 | 3 | 361 | 0.0083102
0.5 | 8 | 2.6 | 0.5 | 61 | 0.0081967
0.5 | 8 | 2.6 | 1 | 123 | 0.0081301
0.5 | 8 | 2.6 | 1.5 | 184 | 0.0081522
0.5 | 8 | 2.6 | 2 | 245 | 0.0081633
0.5 | 8 | 2.6 | 2.5 | 307 | 0.0081433
0.5 | 8 | 2.6 | 3 | 368 | 0.0081522
0.5 | 8 | 2.8 | 0.5 | 63 | 0.0079365
0.5 | 8 | 2.8 | 1 | 125 | 0.008
0.5 | 8 | 2.8 | 1.5 | 188 | 0.0079787
0.5 | 8 | 2.8 | 2 | 250 | 0.008
0.5 | 8 | 2.8 | 2.5 | 313 | 0.0079872
0.5 | 8 | 2.8 | 3 | 375 | 0.008
0.5 | 8 | 3 | 0.5 | 64 | 0.0078125
0.5 | 8 | 3 | 1 | 127 | 0.007874
0.5 | 8 | 3 | 1.5 | 191 | 0.0078534
0.5 | 8 | 3 | 2 | 255 | 0.0078431
0.5 | 8 | 3 | 2.5 | 318 | 0.0078616
0.5 | 8 | 3 | 3 | 382 | 0.0078534
0.5 | 8.5 | 0.4 | 0.5 | 55 | 0.0090909
0.5 | 8.5 | 0.4 | 1 | 110 | 0.0090909
0.5 | 8.5 | 0.4 | 1.5 | 165 | 0.0090909
0.5 | 8.5 | 0.4 | 2 | 219 | 0.0091324
0.5 | 8.5 | 0.4 | 2.5 | 274 | 0.0091241
0.5 | 8.5 | 0.4 | 3 | 329 | 0.0091185
0.5 | 8.5 | 0.6 | 0.5 | 57 | 0.0087719
0.5 | 8.5 | 0.6 | 1 | 114 | 0.0087719
0.5 | 8.5 | 0.6 | 1.5 | 171 | 0.0087719
0.5 | 8.5 | 0.6 | 2 | 228 | 0.0087719
0.5 | 8.5 | 0.6 | 2.5 | 285 | 0.0087719
0.5 | 8.5 | 0.6 | 3 | 342 | 0.0087719
0.5 | 8.5 | 0.8 | 0.5 | 59 | 0.0084746
0.5 | 8.5 | 0.8 | 1 | 118 | 0.0084746
0.5 | 8.5 | 0.8 | 1.5 | 177 | 0.0084746
0.5 | 8.5 | 0.8 | 2 | 236 | 0.0084746
0.5 | 8.5 | 0.8 | 2.5 | 295 | 0.0084746
0.5 | 8.5 | 0.8 | 3 | 354 | 0.0084746
0.5 | 8.5 | 1 | 0.5 | 61 | 0.0081967
0.5 | 8.5 | 1 | 1 | 122 | 0.0081967
0.5 | 8.5 | 1 | 1.5 | 183 | 0.0081967
0.5 | 8.5 | 1 | 2 | 243 | 0.0082305
0.5 | 8.5 | 1 | 2.5 | 304 | 0.0082237
0.5 | 8.5 | 1 | 3 | 365 | 0.0082192
0.5 | 8.5 | 1.2 | 0.5 | 63 | 0.0079365
0.5 | 8.5 | 1.2 | 1 | 125 | 0.008
0.5 | 8.5 | 1.2 | 1.5 | 188 | 0.0079787
0.5 | 8.5 | 1.2 | 2 | 251 | 0.0079681
0.5 | 8.5 | 1.2 | 2.5 | 313 | 0.0079872
0.5 | 8.5 | 1.2 | 3 | 376 | 0.0079787
0.5 | 8.5 | 1.4 | 0.5 | 65 | 0.0076923
0.5 | 8.5 | 1.4 | 1 | 129 | 0.0077519
0.5 | 8.5 | 1.4 | 1.5 | 194 | 0.007732
0.5 | 8.5 | 1.4 | 2 | 258 | 0.0077519
0.5 | 8.5 | 1.4 | 2.5 | 323 | 0.0077399
0.5 | 8.5 | 1.4 | 3 | 387 | 0.0077519
0.5 | 8.5 | 1.6 | 0.5 | 66 | 0.0075758
0.5 | 8.5 | 1.6 | 1 | 132 | 0.0075758
0.5 | 8.5 | 1.6 | 1.5 | 199 | 0.0075377
0.5 | 8.5 | 1.6 | 2 | 265 | 0.0075472
0.5 | 8.5 | 1.6 | 2.5 | 331 | 0.0075529
0.5 | 8.5 | 1.6 | 3 | 397 | 0.0075567
0.5 | 8.5 | 1.8 | 0.5 | 68 | 0.0073529
0.5 | 8.5 | 1.8 | 1 | 136 | 0.0073529
0.5 | 8.5 | 1.8 | 1.5 | 204 | 0.0073529
0.5 | 8.5 | 1.8 | 2 | 271 | 0.0073801
0.5 | 8.5 | 1.8 | 2.5 | 339 | 0.0073746
0.5 | 8.5 | 1.8 | 3 | 407 | 0.007371
0.5 | 8.5 | 2 | 0.5 | 70 | 0.0071429
0.5 | 8.5 | 2 | 1 | 139 | 0.0071942
0.5 | 8.5 | 2 | 1.5 | 209 | 0.007177
0.5 | 8.5 | 2 | 2 | 278 | 0.0071942
0.5 | 8.5 | 2 | 2.5 | 348 | 0.0071839
0.5 | 8.5 | 2 | 3 | 417 | 0.0071942
0.5 | 8.5 | 2.2 | 0.5 | 71 | 0.0070423
0.5 | 8.5 | 2.2 | 1 | 142 | 0.0070423
0.5 | 8.5 | 2.2 | 1.5 | 213 | 0.0070423
0.5 | 8.5 | 2.2 | 2 | 284 | 0.0070423
0.5 | 8.5 | 2.2 | 2.5 | 355 | 0.0070423
0.5 | 8.5 | 2.2 | 3 | 426 | 0.0070423
0.5 | 8.5 | 2.4 | 0.5 | 73 | 0.0068493
0.5 | 8.5 | 2.4 | 1 | 145 | 0.0068966
0.5 | 8.5 | 2.4 | 1.5 | 218 | 0.0068807
0.5 | 8.5 | 2.4 | 2 | 290 | 0.0068966
0.5 | 8.5 | 2.4 | 2.5 | 363 | 0.0068871
0.5 | 8.5 | 2.4 | 3 | 435 | 0.0068966
0.5 | 8.5 | 2.6 | 0.5 | 74 | 0.0067568
0.5 | 8.5 | 2.6 | 1 | 148 | 0.0067568
0.5 | 8.5 | 2.6 | 1.5 | 222 | 0.0067568
0.5 | 8.5 | 2.6 | 2 | 296 | 0.0067568
0.5 | 8.5 | 2.6 | 2.5 | 370 | 0.0067568
0.5 | 8.5 | 2.6 | 3 | 444 | 0.0067568
0.5 | 8.5 | 2.8 | 0.5 | 75 | 0.0066667
0.5 | 8.5 | 2.8 | 1 | 151 | 0.0066225
0.5 | 8.5 | 2.8 | 1.5 | 226 | 0.0066372
0.5 | 8.5 | 2.8 | 2 | 301 | 0.0066445
0.5 | 8.5 | 2.8 | 2.5 | 377 | 0.0066313
0.5 | 8.5 | 2.8 | 3 | 452 | 0.0066372
0.5 | 8.5 | 3 | 0.5 | 77 | 0.0064935
0.5 | 8.5 | 3 | 1 | 153 | 0.0065359
0.5 | 8.5 | 3 | 1.5 | 230 | 0.0065217
0.5 | 8.5 | 3 | 2 | 307 | 0.0065147
0.5 | 8.5 | 3 | 2.5 | 383 | 0.0065274
0.5 | 8.5 | 3 | 3 | 460 | 0.0065217
5 | 7 | 0.4 | 0.5 | 23 | 0.021739
5 | 7 | 0.4 | 1 | 46 | 0.021739
5 | 7 | 0.4 | 1.5 | 70 | 0.021429
5 | 7 | 0.4 | 2 | 93 | 0.021505
5 | 7 | 0.4 | 2.5 | 116 | 0.021552
5 | 7 | 0.4 | 3 | 139 | 0.021583
5 | 7 | 0.6 | 0.5 | 24 | 0.020833
5 | 7 | 0.6 | 1 | 48 | 0.020833
5 | 7 | 0.6 | 1.5 | 72 | 0.020833
5 | 7 | 0.6 | 2 | 95 | 0.021053
5 | 7 | 0.6 | 2.5 | 119 | 0.021008
5 | 7 | 0.6 | 3 | 143 | 0.020979
5 | 7 | 0.8 | 0.5 | 24 | 0.020833
5 | 7 | 0.8 | 1 | 49 | 0.020408
5 | 7 | 0.8 | 1.5 | 73 | 0.020548
5 | 7 | 0.8 | 2 | 97 | 0.020619
5 | 7 | 0.8 | 2.5 | 122 | 0.020492
5 | 7 | 0.8 | 3 | 146 | 0.020548
5 | 7 | 1 | 0.5 | 25 | 0.02
5 | 7 | 1 | 1 | 50 | 0.02
5 | 7 | 1 | 1.5 | 75 | 0.02
5 | 7 | 1 | 2 | 99 | 0.020202
5 | 7 | 1 | 2.5 | 124 | 0.020161
5 | 7 | 1 | 3 | 149 | 0.020134
5 | 7 | 1.2 | 0.5 | 25 | 0.02
5 | 7 | 1.2 | 1 | 51 | 0.019608
5 | 7 | 1.2 | 1.5 | 76 | 0.019737
5 | 7 | 1.2 | 2 | 101 | 0.019802
5 | 7 | 1.2 | 2.5 | 127 | 0.019685
5 | 7 | 1.2 | 3 | 152 | 0.019737
5 | 7 | 1.4 | 0.5 | 26 | 0.019231
5 | 7 | 1.4 | 1 | 52 | 0.019231
5 | 7 | 1.4 | 1.5 | 78 | 0.019231
5 | 7 | 1.4 | 2 | 103 | 0.019417
5 | 7 | 1.4 | 2.5 | 129 | 0.01938
5 | 7 | 1.4 | 3 | 155 | 0.019355
5 | 7 | 1.6 | 0.5 | 26 | 0.019231
5 | 7 | 1.6 | 1 | 53 | 0.018868
5 | 7 | 1.6 | 1.5 | 79 | 0.018987
5 | 7 | 1.6 | 2 | 105 | 0.019048
5 | 7 | 1.6 | 2.5 | 132 | 0.018939
5 | 7 | 1.6 | 3 | 158 | 0.018987
5 | 7 | 1.8 | 0.5 | 27 | 0.018519
5 | 7 | 1.8 | 1 | 54 | 0.018519
5 | 7 | 1.8 | 1.5 | 81 | 0.018519
5 | 7 | 1.8 | 2 | 108 | 0.018519
5 | 7 | 1.8 | 2.5 | 135 | 0.018519
5 | 7 | 1.8 | 3 | 162 | 0.018519
5 | 7 | 2 | 0.5 | 28 | 0.017857
5 | 7 | 2 | 1 | 55 | 0.018182
5 | 7 | 2 | 1.5 | 83 | 0.018072
5 | 7 | 2 | 2 | 110 | 0.018182
5 | 7 | 2 | 2.5 | 138 | 0.018116
5 | 7 | 2 | 3 | 165 | 0.018182
5 | 7 | 2.2 | 0.5 | 28 | 0.017857
5 | 7 | 2.2 | 1 | 56 | 0.017857
5 | 7 | 2.2 | 1.5 | 85 | 0.017647
5 | 7 | 2.2 | 2 | 113 | 0.017699
5 | 7 | 2.2 | 2.5 | 141 | 0.01773
5 | 7 | 2.2 | 3 | 169 | 0.017751
5 | 7 | 2.4 | 0.5 | 29 | 0.017241
5 | 7 | 2.4 | 1 | 57 | 0.017544
5 | 7 | 2.4 | 1.5 | 86 | 0.017442
5 | 7 | 2.4 | 2 | 115 | 0.017391
5 | 7 | 2.4 | 2.5 | 143 | 0.017483
5 | 7 | 2.4 | 3 | 172 | 0.017442
5 | 7 | 2.6 | 0.5 | 29 | 0.017241
5 | 7 | 2.6 | 1 | 58 | 0.017241
5 | 7 | 2.6 | 1.5 | 88 | 0.017045
5 | 7 | 2.6 | 2 | 117 | 0.017094
5 | 7 | 2.6 | 2.5 | 146 | 0.017123
5 | 7 | 2.6 | 3 | 175 | 0.017143
5 | 7 | 2.8 | 0.5 | 30 | 0.016667
5 | 7 | 2.8 | 1 | 59 | 0.016949
5 | 7 | 2.8 | 1.5 | 89 | 0.016854
5 | 7 | 2.8 | 2 | 119 | 0.016807
5 | 7 | 2.8 | 2.5 | 148 | 0.016892
5 | 7 | 2.8 | 3 | 178 | 0.016854
5 | 7 | 3 | 0.5 | 30 | 0.016667
5 | 7 | 3 | 1 | 61 | 0.016393
5 | 7 | 3 | 1.5 | 91 | 0.016484
5 | 7 | 3 | 2 | 121 | 0.016529
5 | 7 | 3 | 2.5 | 152 | 0.016447
5 | 7 | 3 | 3 | 182 | 0.016484
5 | 7.5 | 0.4 | 0.5 | 28 | 0.017857
5 | 7.5 | 0.4 | 1 | 55 | 0.018182
5 | 7.5 | 0.4 | 1.5 | 83 | 0.018072
5 | 7.5 | 0.4 | 2 | 111 | 0.018018
5 | 7.5 | 0.4 | 2.5 | 138 | 0.018116
5 | 7.5 | 0.4 | 3 | 166 | 0.018072
5 | 7.5 | 0.6 | 0.5 | 29 | 0.017241
5 | 7.5 | 0.6 | 1 | 57 | 0.017544
5 | 7.5 | 0.6 | 1.5 | 86 | 0.017442
5 | 7.5 | 0.6 | 2 | 114 | 0.017544
5 | 7.5 | 0.6 | 2.5 | 143 | 0.017483
5 | 7.5 | 0.6 | 3 | 171 | 0.017544
5 | 7.5 | 0.8 | 0.5 | 29 | 0.017241
5 | 7.5 | 0.8 | 1 | 58 | 0.017241
5 | 7.5 | 0.8 | 1.5 | 88 | 0.017045
5 | 7.5 | 0.8 | 2 | 117 | 0.017094
5 | 7.5 | 0.8 | 2.5 | 146 | 0.017123
5 | 7.5 | 0.8 | 3 | 175 | 0.017143
5 | 7.5 | 1 | 0.5 | 30 | 0.016667
5 | 7.5 | 1 | 1 | 60 | 0.016667
5 | 7.5 | 1 | 1.5 | 90 | 0.016667
5 | 7.5 | 1 | 2 | 119 | 0.016807
5 | 7.5 | 1 | 2.5 | 149 | 0.016779
5 | 7.5 | 1 | 3 | 179 | 0.01676
5 | 7.5 | 1.2 | 0.5 | 31 | 0.016129
5 | 7.5 | 1.2 | 1 | 61 | 0.016393
5 | 7.5 | 1.2 | 1.5 | 92 | 0.016304
5 | 7.5 | 1.2 | 2 | 122 | 0.016393
5 | 7.5 | 1.2 | 2.5 | 153 | 0.01634
5 | 7.5 | 1.2 | 3 | 183 | 0.016393
5 | 7.5 | 1.4 | 0.5 | 31 | 0.016129
5 | 7.5 | 1.4 | 1 | 62 | 0.016129
5 | 7.5 | 1.4 | 1.5 | 94 | 0.015957
5 | 7.5 | 1.4 | 2 | 125 | 0.016
5 | 7.5 | 1.4 | 2.5 | 156 | 0.016026
5 | 7.5 | 1.4 | 3 | 187 | 0.016043
5 | 7.5 | 1.6 | 0.5 | 32 | 0.015625
5 | 7.5 | 1.6 | 1 | 64 | 0.015625
5 | 7.5 | 1.6 | 1.5 | 96 | 0.015625
5 | 7.5 | 1.6 | 2 | 128 | 0.015625
5 | 7.5 | 1.6 | 2.5 | 160 | 0.015625
5 | 7.5 | 1.6 | 3 | 192 | 0.015625
5 | 7.5 | 1.8 | 0.5 | 33 | 0.015152
5 | 7.5 | 1.8 | 1 | 65 | 0.015385
5 | 7.5 | 1.8 | 1.5 | 98 | 0.015306
5 | 7.5 | 1.8 | 2 | 131 | 0.015267
5 | 7.5 | 1.8 | 2.5 | 163 | 0.015337
5 | 7.5 | 1.8 | 3 | 196 | 0.015306
5 | 7.5 | 2 | 0.5 | 33 | 0.015152
5 | 7.5 | 2 | 1 | 67 | 0.014925
5 | 7.5 | 2 | 1.5 | 100 | 0.015
5 | 7.5 | 2 | 2 | 133 | 0.015038
5 | 7.5 | 2 | 2.5 | 167 | 0.01497
5 | 7.5 | 2 | 3 | 200 | 0.015
5 | 7.5 | 2.2 | 0.5 | 34 | 0.014706
5 | 7.5 | 2.2 | 1 | 68 | 0.014706
5 | 7.5 | 2.2 | 1.5 | 102 | 0.014706
5 | 7.5 | 2.2 | 2 | 136 | 0.014706
5 | 7.5 | 2.2 | 2.5 | 170 | 0.014706
5 | 7.5 | 2.2 | 3 | 204 | 0.014706
5 | 7.5 | 2.4 | 0.5 | 35 | 0.014286
5 | 7.5 | 2.4 | 1 | 70 | 0.014286
5 | 7.5 | 2.4 | 1.5 | 105 | 0.014286
5 | 7.5 | 2.4 | 2 | 139 | 0.014388
5 | 7.5 | 2.4 | 2.5 | 174 | 0.014368
5 | 7.5 | 2.4 | 3 | 209 | 0.014354
5 | 7.5 | 2.6 | 0.5 | 36 | 0.013889
5 | 7.5 | 2.6 | 1 | 71 | 0.014085
5 | 7.5 | 2.6 | 1.5 | 107 | 0.014019
5 | 7.5 | 2.6 | 2 | 142 | 0.014085
5 | 7.5 | 2.6 | 2.5 | 178 | 0.014045
5 | 7.5 | 2.6 | 3 | 213 | 0.014085
5 | 7.5 | 2.8 | 0.5 | 36 | 0.013889
5 | 7.5 | 2.8 | 1 | 72 | 0.013889
5 | 7.5 | 2.8 | 1.5 | 109 | 0.013761
5 | 7.5 | 2.8 | 2 | 145 | 0.013793
5 | 7.5 | 2.8 | 2.5 | 181 | 0.013812
5 | 7.5 | 2.8 | 3 | 217 | 0.013825
5 | 7.5 | 3 | 0.5 | 37 | 0.013514
5 | 7.5 | 3 | 1 | 74 | 0.013514
5 | 7.5 | 3 | 1.5 | 111 | 0.013514
5 | 7.5 | 3 | 2 | 147 | 0.013605
5 | 7.5 | 3 | 2.5 | 184 | 0.013587
5 | 7.5 | 3 | 3 | 221 | 0.013575
5 | 8 | 0.4 | 0.5 | 33 | 0.015152
5 | 8 | 0.4 | 1 | 66 | 0.015152
5 | 8 | 0.4 | 1.5 | 99 | 0.015152
5 | 8 | 0.4 | 2 | 132 | 0.015152
5 | 8 | 0.4 | 2.5 | 165 | 0.015152
5 | 8 | 0.4 | 3 | 198 | 0.015152
5 | 8 | 0.6 | 0.5 | 34 | 0.014706
5 | 8 | 0.6 | 1 | 68 | 0.014706
5 | 8 | 0.6 | 1.5 | 102 | 0.014706
5 | 8 | 0.6 | 2 | 136 | 0.014706
5 | 8 | 0.6 | 2.5 | 170 | 0.014706
5 | 8 | 0.6 | 3 | 204 | 0.014706
5 | 8 | 0.8 | 0.5 | 35 | 0.014286
5 | 8 | 0.8 | 1 | 70 | 0.014286
5 | 8 | 0.8 | 1.5 | 105 | 0.014286
5 | 8 | 0.8 | 2 | 140 | 0.014286
5 | 8 | 0.8 | 2.5 | 175 | 0.014286
5 | 8 | 0.8 | 3 | 210 | 0.014286
5 | 8 | 1 | 0.5 | 36 | 0.013889
5 | 8 | 1 | 1 | 72 | 0.013889
5 | 8 | 1 | 1.5 | 108 | 0.013889
5 | 8 | 1 | 2 | 144 | 0.013889
5 | 8 | 1 | 2.5 | 180 | 0.013889
5 | 8 | 1 | 3 | 216 | 0.013889
5 | 8 | 1.2 | 0.5 | 37 | 0.013514
5 | 8 | 1.2 | 1 | 74 | 0.013514
5 | 8 | 1.2 | 1.5 | 111 | 0.013514
5 | 8 | 1.2 | 2 | 147 | 0.013605
5 | 8 | 1.2 | 2.5 | 184 | 0.013587
5 | 8 | 1.2 | 3 | 221 | 0.013575
5 | 8 | 1.4 | 0.5 | 38 | 0.013158
5 | 8 | 1.4 | 1 | 76 | 0.013158
5 | 8 | 1.4 | 1.5 | 114 | 0.013158
5 | 8 | 1.4 | 2 | 151 | 0.013245
5 | 8 | 1.4 | 2.5 | 189 | 0.013228
5 | 8 | 1.4 | 3 | 227 | 0.013216
5 | 8 | 1.6 | 0.5 | 39 | 0.012821
5 | 8 | 1.6 | 1 | 77 | 0.012987
5 | 8 | 1.6 | 1.5 | 116 | 0.012931
5 | 8 | 1.6 | 2 | 155 | 0.012903
5 | 8 | 1.6 | 2.5 | 193 | 0.012953
5 | 8 | 1.6 | 3 | 232 | 0.012931
5 | 8 | 1.8 | 0.5 | 40 | 0.0125
5 | 8 | 1.8 | 1 | 79 | 0.012658
5 | 8 | 1.8 | 1.5 | 119 | 0.012605
5 | 8 | 1.8 | 2 | 159 | 0.012579
5 | 8 | 1.8 | 2.5 | 198 | 0.012626
5 | 8 | 1.8 | 3 | 238 | 0.012605
5 | 8 | 2 | 0.5 | 41 | 0.012195
5 | 8 | 2 | 1 | 81 | 0.012346
5 | 8 | 2 | 1.5 | 122 | 0.012295
5 | 8 | 2 | 2 | 162 | 0.012346
5 | 8 | 2 | 2.5 | 203 | 0.012315
5 | 8 | 2 | 3 | 243 | 0.012346
5 | 8 | 2.2 | 0.5 | 41 | 0.012195
5 | 8 | 2.2 | 1 | 83 | 0.012048
5 | 8 | 2.2 | 1.5 | 124 | 0.012097
5 | 8 | 2.2 | 2 | 165 | 0.012121
5 | 8 | 2.2 | 2.5 | 207 | 0.012077
5 | 8 | 2.2 | 3 | 248 | 0.012097
5 | 8 | 2.4 | 0.5 | 42 | 0.011905
5 | 8 | 2.4 | 1 | 84 | 0.011905
5 | 8 | 2.4 | 1.5 | 127 | 0.011811
5 | 8 | 2.4 | 2 | 169 | 0.011834
5 | 8 | 2.4 | 2.5 | 211 | 0.011848
5 | 8 | 2.4 | 3 | 253 | 0.011858
5 | 8 | 2.6 | 0.5 | 43 | 0.011628
5 | 8 | 2.6 | 1 | 86 | 0.011628
5 | 8 | 2.6 | 1.5 | 129 | 0.011628
5 | 8 | 2.6 | 2 | 172 | 0.011628
5 | 8 | 2.6 | 2.5 | 215 | 0.011628
5 | 8 | 2.6 | 3 | 258 | 0.011628
5 | 8 | 2.8 | 0.5 | 44 | 0.011364
5 | 8 | 2.8 | 1 | 88 | 0.011364
5 | 8 | 2.8 | 1.5 | 132 | 0.011364
5 | 8 | 2.8 | 2 | 175 | 0.011429
5 | 8 | 2.8 | 2.5 | 219 | 0.011416
5 | 8 | 2.8 | 3 | 263 | 0.011407
5 | 8 | 3 | 0.5 | 45 | 0.011111
5 | 8 | 3 | 1 | 89 | 0.011236
5 | 8 | 3 | 1.5 | 134 | 0.011194
5 | 8 | 3 | 2 | 179 | 0.011173
5 | 8 | 3 | 2.5 | 223 | 0.011211
5 | 8 | 3 | 3 | 268 | 0.011194
5 | 8.5 | 0.4 | 0.5 | 39 | 0.012821
5 | 8.5 | 0.4 | 1 | 79 | 0.012658
5 | 8.5 | 0.4 | 1.5 | 118 | 0.012712
5 | 8.5 | 0.4 | 2 | 157 | 0.012739
5 | 8.5 | 0.4 | 2.5 | 197 | 0.01269
5 | 8.5 | 0.4 | 3 | 236 | 0.012712
5 | 8.5 | 0.6 | 0.5 | 41 | 0.012195
5 | 8.5 | 0.6 | 1 | 81 | 0.012346
5 | 8.5 | 0.6 | 1.5 | 122 | 0.012295
5 | 8.5 | 0.6 | 2 | 163 | 0.01227
5 | 8.5 | 0.6 | 2.5 | 203 | 0.012315
5 | 8.5 | 0.6 | 3 | 244 | 0.012295
5 | 8.5 | 0.8 | 0.5 | 42 | 0.011905
5 | 8.5 | 0.8 | 1 | 84 | 0.011905
5 | 8.5 | 0.8 | 1.5 | 126 | 0.011905
5 | 8.5 | 0.8 | 2 | 168 | 0.011905
5 | 8.5 | 0.8 | 2.5 | 210 | 0.011905
5 | 8.5 | 0.8 | 3 | 252 | 0.011905
5 | 8.5 | 1 | 0.5 | 43 | 0.011628
5 | 8.5 | 1 | 1 | 87 | 0.011494
5 | 8.5 | 1 | 1.5 | 130 | 0.011538
5 | 8.5 | 1 | 2 | 173 | 0.011561
5 | 8.5 | 1 | 2.5 | 217 | 0.011521
5 | 8.5 | 1 | 3 | 260 | 0.011538
5 | 8.5 | 1.2 | 0.5 | 45 | 0.011111
5 | 8.5 | 1.2 | 1 | 89 | 0.011236
5 | 8.5 | 1.2 | 1.5 | 134 | 0.011194
5 | 8.5 | 1.2 | 2 | 178 | 0.011236
5 | 8.5 | 1.2 | 2.5 | 223 | 0.011211
5 | 8.5 | 1.2 | 3 | 267 | 0.011236
5 | 8.5 | 1.4 | 0.5 | 46 | 0.01087
5 | 8.5 | 1.4 | 1 | 91 | 0.010989
5 | 8.5 | 1.4 | 1.5 | 137 | 0.010949
5 | 8.5 | 1.4 | 2 | 183 | 0.010929
5 | 8.5 | 1.4 | 2.5 | 228 | 0.010965
5 | 8.5 | 1.4 | 3 | 274 | 0.010949
5 | 8.5 | 1.6 | 0.5 | 47 | 0.010638
5 | 8.5 | 1.6 | 1 | 94 | 0.010638
5 | 8.5 | 1.6 | 1.5 | 141 | 0.010638
5 | 8.5 | 1.6 | 2 | 187 | 0.010695
5 | 8.5 | 1.6 | 2.5 | 234 | 0.010684
5 | 8.5 | 1.6 | 3 | 281 | 0.010676
5 | 8.5 | 1.8 | 0.5 | 48 | 0.010417
5 | 8.5 | 1.8 | 1 | 96 | 0.010417
5 | 8.5 | 1.8 | 1.5 | 144 | 0.010417
5 | 8.5 | 1.8 | 2 | 191 | 0.010471
5 | 8.5 | 1.8 | 2.5 | 239 | 0.01046
5 | 8.5 | 1.8 | 3 | 287 | 0.010453
5 | 8.5 | 2 | 0.5 | 49 | 0.010204
5 | 8.5 | 2 | 1 | 98 | 0.010204
5 | 8.5 | 2 | 1.5 | 147 | 0.010204
5 | 8.5 | 2 | 2 | 196 | 0.010204
5 | 8.5 | 2 | 2.5 | 245 | 0.010204
5 | 8.5 | 2 | 3 | 294 | 0.010204
5 | 8.5 | 2.2 | 0.5 | 50 | 0.01
5 | 8.5 | 2.2 | 1 | 100 | 0.01
5 | 8.5 | 2.2 | 1.5 | 150 | 0.01
5 | 8.5 | 2.2 | 2 | 200 | 0.01
5 | 8.5 | 2.2 | 2.5 | 250 | 0.01
5 | 8.5 | 2.2 | 3 | 300 | 0.01
5 | 8.5 | 2.4 | 0.5 | 51 | 0.0098039
5 | 8.5 | 2.4 | 1 | 102 | 0.0098039
5 | 8.5 | 2.4 | 1.5 | 153 | 0.0098039
5 | 8.5 | 2.4 | 2 | 204 | 0.0098039
5 | 8.5 | 2.4 | 2.5 | 255 | 0.0098039
5 | 8.5 | 2.4 | 3 | 306 | 0.0098039
5 | 8.5 | 2.6 | 0.5 | 52 | 0.0096154
5 | 8.5 | 2.6 | 1 | 104 | 0.0096154
5 | 8.5 | 2.6 | 1.5 | 156 | 0.0096154
5 | 8.5 | 2.6 | 2 | 208 | 0.0096154
5 | 8.5 | 2.6 | 2.5 | 260 | 0.0096154
5 | 8.5 | 2.6 | 3 | 312 | 0.0096154
5 | 8.5 | 2.8 | 0.5 | 53 | 0.009434
5 | 8.5 | 2.8 | 1 | 106 | 0.009434
5 | 8.5 | 2.8 | 1.5 | 159 | 0.009434
5 | 8.5 | 2.8 | 2 | 212 | 0.009434
5 | 8.5 | 2.8 | 2.5 | 265 | 0.009434
5 | 8.5 | 2.8 | 3 | 318 | 0.009434
5 | 8.5 | 3 | 0.5 | 54 | 0.0092593
5 | 8.5 | 3 | 1 | 108 | 0.0092593
5 | 8.5 | 3 | 1.5 | 162 | 0.0092593
5 | 8.5 | 3 | 2 | 216 | 0.0092593
5 | 8.5 | 3 | 2.5 | 270 | 0.0092593
5 | 8.5 | 3 | 3 | 324 | 0.0092593
10 | 7 | 0.4 | 0.5 | 17 | 0.029412
10 | 7 | 0.4 | 1 | 35 | 0.028571
10 | 7 | 0.4 | 1.5 | 52 | 0.028846
10 | 7 | 0.4 | 2 | 69 | 0.028986
10 | 7 | 0.4 | 2.5 | 87 | 0.028736
10 | 7 | 0.4 | 3 | 104 | 0.028846
10 | 7 | 0.6 | 0.5 | 18 | 0.027778
10 | 7 | 0.6 | 1 | 36 | 0.027778
10 | 7 | 0.6 | 1.5 | 54 | 0.027778
10 | 7 | 0.6 | 2 | 71 | 0.028169
10 | 7 | 0.6 | 2.5 | 89 | 0.02809
10 | 7 | 0.6 | 3 | 107 | 0.028037
10 | 7 | 0.8 | 0.5 | 18 | 0.027778
10 | 7 | 0.8 | 1 | 37 | 0.027027
10 | 7 | 0.8 | 1.5 | 55 | 0.027273
10 | 7 | 0.8 | 2 | 73 | 0.027397
10 | 7 | 0.8 | 2.5 | 92 | 0.027174
10 | 7 | 0.8 | 3 | 110 | 0.027273
10 | 7 | 1 | 0.5 | 19 | 0.026316
10 | 7 | 1 | 1 | 37 | 0.027027
10 | 7 | 1 | 1.5 | 56 | 0.026786
10 | 7 | 1 | 2 | 75 | 0.026667
10 | 7 | 1 | 2.5 | 93 | 0.026882
10 | 7 | 1 | 3 | 112 | 0.026786
10 | 7 | 1.2 | 0.5 | 19 | 0.026316
10 | 7 | 1.2 | 1 | 38 | 0.026316
10 | 7 | 1.2 | 1.5 | 57 | 0.026316
10 | 7 | 1.2 | 2 | 76 | 0.026316
10 | 7 | 1.2 | 2.5 | 95 | 0.026316
10 | 7 | 1.2 | 3 | 114 | 0.026316
10 | 7 | 1.4 | 0.5 | 19 | 0.026316
10 | 7 | 1.4 | 1 | 39 | 0.025641
10 | 7 | 1.4 | 1.5 | 58 | 0.025862
10 | 7 | 1.4 | 2 | 77 | 0.025974
10 | 7 | 1.4 | 2.5 | 97 | 0.025773
10 | 7 | 1.4 | 3 | 116 | 0.025862
10 | 7 | 1.6 | 0.5 | 20 | 0.025
10 | 7 | 1.6 | 1 | 40 | 0.025
10 | 7 | 1.6 | 1.5 | 60 | 0.025
10 | 7 | 1.6 | 2 | 79 | 0.025316
10 | 7 | 1.6 | 2.5 | 99 | 0.025253
10 | 7 | 1.6 | 3 | 119 | 0.02521
10 | 7 | 1.8 | 0.5 | 20 | 0.025
10 | 7 | 1.8 | 1 | 41 | 0.02439
10 | 7 | 1.8 | 1.5 | 61 | 0.02459
10 | 7 | 1.8 | 2 | 81 | 0.024691
10 | 7 | 1.8 | 2.5 | 102 | 0.02451
10 | 7 | 1.8 | 3 | 122 | 0.02459
10 | 7 | 2 | 0.5 | 21 | 0.02381
10 | 7 | 2 | 1 | 41 | 0.02439
10 | 7 | 2 | 1.5 | 62 | 0.024194
10 | 7 | 2 | 2 | 83 | 0.024096
10 | 7 | 2 | 2.5 | 103 | 0.024272
10 | 7 | 2 | 3 | 124 | 0.024194
10 | 7 | 2.2 | 0.5 | 21 | 0.02381
10 | 7 | 2.2 | 1 | 42 | 0.02381
10 | 7 | 2.2 | 1.5 | 64 | 0.023438
10 | 7 | 2.2 | 2 | 85 | 0.023529
10 | 7 | 2.2 | 2.5 | 106 | 0.023585
10 | 7 | 2.2 | 3 | 127 | 0.023622
10 | 7 | 2.4 | 0.5 | 22 | 0.022727
10 | 7 | 2.4 | 1 | 43 | 0.023256
10 | 7 | 2.4 | 1.5 | 65 | 0.023077
10 | 7 | 2.4 | 2 | 86 | 0.023256
10 | 7 | 2.4 | 2.5 | 108 | 0.023148
10 | 7 | 2.4 | 3 | 129 | 0.023256
10 | 7 | 2.6 | 0.5 | 22 | 0.022727
10 | 7 | 2.6 | 1 | 44 | 0.022727
10 | 7 | 2.6 | 1.5 | 66 | 0.022727
10 | 7 | 2.6 | 2 | 87 | 0.022989
10 | 7 | 2.6 | 2.5 | 109 | 0.022936
10 | 7 | 2.6 | 3 | 131 | 0.022901
10 | 7 | 2.8 | 0.5 | 22 | 0.022727
10 | 7 | 2.8 | 1 | 45 | 0.022222
10 | 7 | 2.8 | 1.5 | 67 | 0.022388
10 | 7 | 2.8 | 2 | 89 | 0.022472
10 | 7 | 2.8 | 2.5 | 112 | 0.022321
10 | 7 | 2.8 | 3 | 134 | 0.022388
10 | 7 | 3 | 0.5 | 23 | 0.021739
10 | 7 | 3 | 1 | 46 | 0.021739
10 | 7 | 3 | 1.5 | 69 | 0.021739
10 | 7 | 3 | 2 | 91 | 0.021978
10 | 7 | 3 | 2.5 | 114 | 0.02193
10 | 7 | 3 | 3 | 137 | 0.021898
10 | 7.5 | 0.4 | 0.5 | 21 | 0.02381
10 | 7.5 | 0.4 | 1 | 42 | 0.02381
10 | 7.5 | 0.4 | 1.5 | 63 | 0.02381
10 | 7.5 | 0.4 | 2 | 83 | 0.024096
10 | 7.5 | 0.4 | 2.5 | 104 | 0.024038
10 | 7.5 | 0.4 | 3 | 125 | 0.024
10 | 7.5 | 0.6 | 0.5 | 21 | 0.02381
10 | 7.5 | 0.6 | 1 | 43 | 0.023256
10 | 7.5 | 0.6 | 1.5 | 64 | 0.023438
10 | 7.5 | 0.6 | 2 | 85 | 0.023529
10 | 7.5 | 0.6 | 2.5 | 107 | 0.023364
10 | 7.5 | 0.6 | 3 | 128 | 0.023438
10 | 7.5 | 0.8 | 0.5 | 22 | 0.022727
10 | 7.5 | 0.8 | 1 | 44 | 0.022727
10 | 7.5 | 0.8 | 1.5 | 66 | 0.022727
10 | 7.5 | 0.8 | 2 | 87 | 0.022989
10 | 7.5 | 0.8 | 2.5 | 109 | 0.022936
10 | 7.5 | 0.8 | 3 | 131 | 0.022901
10 | 7.5 | 1 | 0.5 | 22 | 0.022727
10 | 7.5 | 1 | 1 | 45 | 0.022222
10 | 7.5 | 1 | 1.5 | 67 | 0.022388
10 | 7.5 | 1 | 2 | 89 | 0.022472
10 | 7.5 | 1 | 2.5 | 112 | 0.022321
10 | 7.5 | 1 | 3 | 134 | 0.022388
10 | 7.5 | 1.2 | 0.5 | 23 | 0.021739
10 | 7.5 | 1.2 | 1 | 46 | 0.021739
10 | 7.5 | 1.2 | 1.5 | 69 | 0.021739
10 | 7.5 | 1.2 | 2 | 91 | 0.021978
10 | 7.5 | 1.2 | 2.5 | 114 | 0.02193
10 | 7.5 | 1.2 | 3 | 137 | 0.021898
10 | 7.5 | 1.4 | 0.5 | 23 | 0.021739
10 | 7.5 | 1.4 | 1 | 47 | 0.021277
10 | 7.5 | 1.4 | 1.5 | 70 | 0.021429
10 | 7.5 | 1.4 | 2 | 93 | 0.021505
10 | 7.5 | 1.4 | 2.5 | 117 | 0.021368
10 | 7.5 | 1.4 | 3 | 140 | 0.021429
10 | 7.5 | 1.6 | 0.5 | 24 | 0.020833
10 | 7.5 | 1.6 | 1 | 48 | 0.020833
10 | 7.5 | 1.6 | 1.5 | 72 | 0.020833
10 | 7.5 | 1.6 | 2 | 96 | 0.020833
10 | 7.5 | 1.6 | 2.5 | 120 | 0.020833
10 | 7.5 | 1.6 | 3 | 144 | 0.020833
10 | 7.5 | 1.8 | 0.5 | 25 | 0.02
10 | 7.5 | 1.8 | 1 | 49 | 0.020408
10 | 7.5 | 1.8 | 1.5 | 74 | 0.02027
10 | 7.5 | 1.8 | 2 | 98 | 0.020408
10 | 7.5 | 1.8 | 2.5 | 123 | 0.020325
10 | 7.5 | 1.8 | 3 | 147 | 0.020408
10 | 7.5 | 2 | 0.5 | 25 | 0.02
10 | 7.5 | 2 | 1 | 50 | 0.02
10 | 7.5 | 2 | 1.5 | 75 | 0.02
10 | 7.5 | 2 | 2 | 100 | 0.02
10 | 7.5 | 2 | 2.5 | 125 | 0.02
10 | 7.5 | 2 | 3 | 150 | 0.02
10 | 7.5 | 2.2 | 0.5 | 26 | 0.019231
10 | 7.5 | 2.2 | 1 | 51 | 0.019608
10 | 7.5 | 2.2 | 1.5 | 77 | 0.019481
10 | 7.5 | 2.2 | 2 | 102 | 0.019608
10 | 7.5 | 2.2 | 2.5 | 128 | 0.019531
10 | 7.5 | 2.2 | 3 | 153 | 0.019608
10 | 7.5 | 2.4 | 0.5 | 26 | 0.019231
10 | 7.5 | 2.4 | 1 | 52 | 0.019231
10 | 7.5 | 2.4 | 1.5 | 79 | 0.018987
10 | 7.5 | 2.4 | 2 | 105 | 0.019048
10 | 7.5 | 2.4 | 2.5 | 131 | 0.019084
10 | 7.5 | 2.4 | 3 | 157 | 0.019108
10 | 7.5 | 2.6 | 0.5 | 27 | 0.018519
10 | 7.5 | 2.6 | 1 | 53 | 0.018868
10 | 7.5 | 2.6 | 1.5 | 80 | 0.01875
10 | 7.5 | 2.6 | 2 | 107 | 0.018692
10 | 7.5 | 2.6 | 2.5 | 133 | 0.018797
10 | 7.5 | 2.6 | 3 | 160 | 0.01875
10 | 7.5 | 2.8 | 0.5 | 27 | 0.018519
10 | 7.5 | 2.8 | 1 | 54 | 0.018519
10 | 7.5 | 2.8 | 1.5 | 82 | 0.018293
10 | 7.5 | 2.8 | 2 | 109 | 0.018349
10 | 7.5 | 2.8 | 2.5 | 136 | 0.018382
10 | 7.5 | 2.8 | 3 | 163 | 0.018405
10 | 7.5 | 3 | 0.5 | 28 | 0.017857
10 | 7.5 | 3 | 1 | 55 | 0.018182
10 | 7.5 | 3 | 1.5 | 83 | 0.018072
10 | 7.5 | 3 | 2 | 111 | 0.018018
10 | 7.5 | 3 | 2.5 | 138 | 0.018116
10 | 7.5 | 3 | 3 | 166 | 0.018072
10 | 8 | 0.4 | 0.5 | 25 | 0.02
10 | 8 | 0.4 | 1 | 50 | 0.02
10 | 8 | 0.4 | 1.5 | 75 | 0.02
10 | 8 | 0.4 | 2 | 99 | 0.020202
10 | 8 | 0.4 | 2.5 | 124 | 0.020161
10 | 8 | 0.4 | 3 | 149 | 0.020134
10 | 8 | 0.6 | 0.5 | 26 | 0.019231
10 | 8 | 0.6 | 1 | 51 | 0.019608
10 | 8 | 0.6 | 1.5 | 77 | 0.019481
10 | 8 | 0.6 | 2 | 102 | 0.019608
10 | 8 | 0.6 | 2.5 | 128 | 0.019531
10 | 8 | 0.6 | 3 | 153 | 0.019608
10 | 8 | 0.8 | 0.5 | 26 | 0.019231
10 | 8 | 0.8 | 1 | 53 | 0.018868
10 | 8 | 0.8 | 1.5 | 79 | 0.018987
10 | 8 | 0.8 | 2 | 105 | 0.019048
10 | 8 | 0.8 | 2.5 | 132 | 0.018939
10 | 8 | 0.8 | 3 | 158 | 0.018987
10 | 8 | 1 | 0.5 | 27 | 0.018519
10 | 8 | 1 | 1 | 54 | 0.018519
10 | 8 | 1 | 1.5 | 81 | 0.018519
10 | 8 | 1 | 2 | 108 | 0.018519
10 | 8 | 1 | 2.5 | 135 | 0.018519
10 | 8 | 1 | 3 | 162 | 0.018519
10 | 8 | 1.2 | 0.5 | 28 | 0.017857
10 | 8 | 1.2 | 1 | 55 | 0.018182
10 | 8 | 1.2 | 1.5 | 83 | 0.018072
10 | 8 | 1.2 | 2 | 111 | 0.018018
10 | 8 | 1.2 | 2.5 | 138 | 0.018116
10 | 8 | 1.2 | 3 | 166 | 0.018072
10 | 8 | 1.4 | 0.5 | 28 | 0.017857
10 | 8 | 1.4 | 1 | 57 | 0.017544
10 | 8 | 1.4 | 1.5 | 85 | 0.017647
10 | 8 | 1.4 | 2 | 113 | 0.017699
10 | 8 | 1.4 | 2.5 | 142 | 0.017606
10 | 8 | 1.4 | 3 | 170 | 0.017647
10 | 8 | 1.6 | 0.5 | 29 | 0.017241
10 | 8 | 1.6 | 1 | 58 | 0.017241
10 | 8 | 1.6 | 1.5 | 87 | 0.017241
10 | 8 | 1.6 | 2 | 116 | 0.017241
10 | 8 | 1.6 | 2.5 | 145 | 0.017241
10 | 8 | 1.6 | 3 | 174 | 0.017241
10 | 8 | 1.8 | 0.5 | 30 | 0.016667
10 | 8 | 1.8 | 1 | 60 | 0.016667
10 | 8 | 1.8 | 1.5 | 90 | 0.016667
10 | 8 | 1.8 | 2 | 119 | 0.016807
10 | 8 | 1.8 | 2.5 | 149 | 0.016779
10 | 8 | 1.8 | 3 | 179 | 0.01676
10 | 8 | 2 | 0.5 | 30 | 0.016667
10 | 8 | 2 | 1 | 61 | 0.016393
10 | 8 | 2 | 1.5 | 91 | 0.016484
10 | 8 | 2 | 2 | 121 | 0.016529
10 | 8 | 2 | 2.5 | 152 | 0.016447
10 | 8 | 2 | 3 | 182 | 0.016484
10 | 8 | 2.2 | 0.5 | 31 | 0.016129
10 | 8 | 2.2 | 1 | 62 | 0.016129
10 | 8 | 2.2 | 1.5 | 93 | 0.016129
10 | 8 | 2.2 | 2 | 124 | 0.016129
10 | 8 | 2.2 | 2.5 | 155 | 0.016129
10 | 8 | 2.2 | 3 | 186 | 0.016129
10 | 8 | 2.4 | 0.5 | 32 | 0.015625
10 | 8 | 2.4 | 1 | 63 | 0.015873
10 | 8 | 2.4 | 1.5 | 95 | 0.015789
10 | 8 | 2.4 | 2 | 127 | 0.015748
10 | 8 | 2.4 | 2.5 | 158 | 0.015823
10 | 8 | 2.4 | 3 | 190 | 0.015789
10 | 8 | 2.6 | 0.5 | 32 | 0.015625
10 | 8 | 2.6 | 1 | 65 | 0.015385
10 | 8 | 2.6 | 1.5 | 97 | 0.015464
10 | 8 | 2.6 | 2 | 129 | 0.015504
10 | 8 | 2.6 | 2.5 | 162 | 0.015432
10 | 8 | 2.6 | 3 | 194 | 0.015464
10 | 8 | 2.8 | 0.5 | 33 | 0.015152
10 | 8 | 2.8 | 1 | 66 | 0.015152
10 | 8 | 2.8 | 1.5 | 99 | 0.015152
10 | 8 | 2.8 | 2 | 131 | 0.015267
10 | 8 | 2.8 | 2.5 | 164 | 0.015244
10 | 8 | 2.8 | 3 | 197 | 0.015228
10 | 8 | 3 | 0.5 | 34 | 0.014706
10 | 8 | 3 | 1 | 67 | 0.014925
10 | 8 | 3 | 1.5 | 101 | 0.014851
10 | 8 | 3 | 2 | 134 | 0.014925
10 | 8 | 3 | 2.5 | 168 | 0.014881
10 | 8 | 3 | 3 | 201 | 0.014925
10 | 8.5 | 0.4 | 0.5 | 30 | 0.016667
10 | 8.5 | 0.4 | 1 | 59 | 0.016949
10 | 8.5 | 0.4 | 1.5 | 89 | 0.016854
10 | 8.5 | 0.4 | 2 | 118 | 0.016949
10 | 8.5 | 0.4 | 2.5 | 148 | 0.016892
10 | 8.5 | 0.4 | 3 | 177 | 0.016949
10 | 8.5 | 0.6 | 0.5 | 31 | 0.016129
10 | 8.5 | 0.6 | 1 | 61 | 0.016393
10 | 8.5 | 0.6 | 1.5 | 92 | 0.016304
10 | 8.5 | 0.6 | 2 | 122 | 0.016393
10 | 8.5 | 0.6 | 2.5 | 153 | 0.01634
10 | 8.5 | 0.6 | 3 | 183 | 0.016393
10 | 8.5 | 0.8 | 0.5 | 32 | 0.015625
10 | 8.5 | 0.8 | 1 | 63 | 0.015873
10 | 8.5 | 0.8 | 1.5 | 95 | 0.015789
10 | 8.5 | 0.8 | 2 | 126 | 0.015873
10 | 8.5 | 0.8 | 2.5 | 158 | 0.015823
10 | 8.5 | 0.8 | 3 | 189 | 0.015873
10 | 8.5 | 1 | 0.5 | 33 | 0.015152
10 | 8.5 | 1 | 1 | 65 | 0.015385
10 | 8.5 | 1 | 1.5 | 98 | 0.015306
10 | 8.5 | 1 | 2 | 130 | 0.015385
10 | 8.5 | 1 | 2.5 | 163 | 0.015337
10 | 8.5 | 1 | 3 | 195 | 0.015385
10 | 8.5 | 1.2 | 0.5 | 33 | 0.015152
10 | 8.5 | 1.2 | 1 | 67 | 0.014925
10 | 8.5 | 1.2 | 1.5 | 100 | 0.015
10 | 8.5 | 1.2 | 2 | 133 | 0.015038
10 | 8.5 | 1.2 | 2.5 | 167 | 0.01497
10 | 8.5 | 1.2 | 3 | 200 | 0.015
10 | 8.5 | 1.4 | 0.5 | 34 | 0.014706
10 | 8.5 | 1.4 | 1 | 69 | 0.014493
10 | 8.5 | 1.4 | 1.5 | 103 | 0.014563
10 | 8.5 | 1.4 | 2 | 137 | 0.014599
10 | 8.5 | 1.4 | 2.5 | 172 | 0.014535
10 | 8.5 | 1.4 | 3 | 206 | 0.014563
10 | 8.5 | 1.6 | 0.5 | 35 | 0.014286
10 | 8.5 | 1.6 | 1 | 70 | 0.014286
10 | 8.5 | 1.6 | 1.5 | 106 | 0.014151
10 | 8.5 | 1.6 | 2 | 141 | 0.014184
10 | 8.5 | 1.6 | 2.5 | 176 | 0.014205
10 | 8.5 | 1.6 | 3 | 211 | 0.014218
10 | 8.5 | 1.8 | 0.5 | 36 | 0.013889
10 | 8.5 | 1.8 | 1 | 72 | 0.013889
10 | 8.5 | 1.8 | 1.5 | 108 | 0.013889
10 | 8.5 | 1.8 | 2 | 143 | 0.013986
10 | 8.5 | 1.8 | 2.5 | 179 | 0.013966
10 | 8.5 | 1.8 | 3 | 215 | 0.013953
10 | 8.5 | 2 | 0.5 | 37 | 0.013514
10 | 8.5 | 2 | 1 | 74 | 0.013514
10 | 8.5 | 2 | 1.5 | 111 | 0.013514
10 | 8.5 | 2 | 2 | 147 | 0.013605
10 | 8.5 | 2 | 2.5 | 184 | 0.013587
10 | 8.5 | 2 | 3 | 221 | 0.013575
10 | 8.5 | 2.2 | 0.5 | 38 | 0.013158
10 | 8.5 | 2.2 | 1 | 75 | 0.013333
10 | 8.5 | 2.2 | 1.5 | 113 | 0.013274
10 | 8.5 | 2.2 | 2 | 150 | 0.013333
10 | 8.5 | 2.2 | 2.5 | 188 | 0.013298
10 | 8.5 | 2.2 | 3 | 225 | 0.013333
10 | 8.5 | 2.4 | 0.5 | 38 | 0.013158
10 | 8.5 | 2.4 | 1 | 77 | 0.012987
10 | 8.5 | 2.4 | 1.5 | 115 | 0.013043
10 | 8.5 | 2.4 | 2 | 153 | 0.013072
10 | 8.5 | 2.4 | 2.5 | 192 | 0.013021
10 | 8.5 | 2.4 | 3 | 230 | 0.013043
10 | 8.5 | 2.6 | 0.5 | 39 | 0.012821
10 | 8.5 | 2.6 | 1 | 78 | 0.012821
10 | 8.5 | 2.6 | 1.5 | 117 | 0.012821
10 | 8.5 | 2.6 | 2 | 156 | 0.012821
10 | 8.5 | 2.6 | 2.5 | 195 | 0.012821
10 | 8.5 | 2.6 | 3 | 234 | 0.012821
10 | 8.5 | 2.8 | 0.5 | 40 | 0.0125
10 | 8.5 | 2.8 | 1 | 80 | 0.0125
10 | 8.5 | 2.8 | 1.5 | 120 | 0.0125
10 | 8.5 | 2.8 | 2 | 159 | 0.012579
10 | 8.5 | 2.8 | 2.5 | 199 | 0.012563
10 | 8.5 | 2.8 | 3 | 239 | 0.012552
10 | 8.5 | 3 | 0.5 | 41 | 0.012195
10 | 8.5 | 3 | 1 | 81 | 0.012346
10 | 8.5 | 3 | 1.5 | 122 | 0.012295
10 | 8.5 | 3 | 2 | 162 | 0.012346
10 | 8.5 | 3 | 2.5 | 203 | 0.012315
10 | 8.5 | 3 | 3 | 243 | 0.012346
15 | 7 | 0.4 | 0.5 | 12 | 0.041667
15 | 7 | 0.4 | 1 | 23 | 0.043478
15 | 7 | 0.4 | 1.5 | 35 | 0.042857
15 | 7 | 0.4 | 2 | 47 | 0.042553
15 | 7 | 0.4 | 2.5 | 58 | 0.043103
15 | 7 | 0.4 | 3 | 70 | 0.042857
15 | 7 | 0.6 | 0.5 | 12 | 0.041667
15 | 7 | 0.6 | 1 | 24 | 0.041667
15 | 7 | 0.6 | 1.5 | 36 | 0.041667
15 | 7 | 0.6 | 2 | 48 | 0.041667
15 | 7 | 0.6 | 2.5 | 60 | 0.041667
15 | 7 | 0.6 | 3 | 72 | 0.041667
15 | 7 | 0.8 | 0.5 | 12 | 0.041667
15 | 7 | 0.8 | 1 | 24 | 0.041667
15 | 7 | 0.8 | 1.5 | 37 | 0.040541
15 | 7 | 0.8 | 2 | 49 | 0.040816
15 | 7 | 0.8 | 2.5 | 61 | 0.040984
15 | 7 | 0.8 | 3 | 73 | 0.041096
15 | 7 | 1 | 0.5 | 13 | 0.038462
15 | 7 | 1 | 1 | 25 | 0.04
15 | 7 | 1 | 1.5 | 38 | 0.039474
15 | 7 | 1 | 2 | 50 | 0.04
15 | 7 | 1 | 2.5 | 63 | 0.039683
15 | 7 | 1 | 3 | 75 | 0.04
15 | 7 | 1.2 | 0.5 | 13 | 0.038462
15 | 7 | 1.2 | 1 | 25 | 0.04
15 | 7 | 1.2 | 1.5 | 38 | 0.039474
15 | 7 | 1.2 | 2 | 51 | 0.039216
15 | 7 | 1.2 | 2.5 | 63 | 0.039683
15 | 7 | 1.2 | 3 | 76 | 0.039474
15 | 7 | 1.4 | 0.5 | 13 | 0.038462
15 | 7 | 1.4 | 1 | 26 | 0.038462
15 | 7 | 1.4 | 1.5 | 39 | 0.038462
15 | 7 | 1.4 | 2 | 52 | 0.038462
15 | 7 | 1.4 | 2.5 | 65 | 0.038462
15 | 7 | 1.4 | 3 | 78 | 0.038462
15 | 7 | 1.6 | 0.5 | 13 | 0.038462
15 | 7 | 1.6 | 1 | 26 | 0.038462
15 | 7 | 1.6 | 1.5 | 40 | 0.0375
15 | 7 | 1.6 | 2 | 53 | 0.037736
15 | 7 | 1.6 | 2.5 | 66 | 0.037879
15 | 7 | 1.6 | 3 | 79 | 0.037975
15 | 7 | 1.8 | 0.5 | 14 | 0.035714
15 | 7 | 1.8 | 1 | 27 | 0.037037
15 | 7 | 1.8 | 1.5 | 41 | 0.036585
15 | 7 | 1.8 | 2 | 54 | 0.037037
15 | 7 | 1.8 | 2.5 | 68 | 0.036765
15 | 7 | 1.8 | 3 | 81 | 0.037037
15 | 7 | 2 | 0.5 | 14 | 0.035714
15 | 7 | 2 | 1 | 28 | 0.035714
15 | 7 | 2 | 1.5 | 42 | 0.035714
15 | 7 | 2 | 2 | 55 | 0.036364
15 | 7 | 2 | 2.5 | 69 | 0.036232
15 | 7 | 2 | 3 | 83 | 0.036145
15 | 7 | 2.2 | 0.5 | 14 | 0.035714
15 | 7 | 2.2 | 1 | 28 | 0.035714
15 | 7 | 2.2 | 1.5 | 43 | 0.034884
15 | 7 | 2.2 | 2 | 57 | 0.035088
15 | 7 | 2.2 | 2.5 | 71 | 0.035211
15 | 7 | 2.2 | 3 | 85 | 0.035294
15 | 7 | 2.4 | 0.5 | 14 | 0.035714
15 | 7 | 2.4 | 1 | 29 | 0.034483
15 | 7 | 2.4 | 1.5 | 43 | 0.034884
15 | 7 | 2.4 | 2 | 57 | 0.035088
15 | 7 | 2.4 | 2.5 | 72 | 0.034722
15 | 7 | 2.4 | 3 | 86 | 0.034884
15 | 7 | 2.6 | 0.5 | 15 | 0.033333
15 | 7 | 2.6 | 1 | 29 | 0.034483
15 | 7 | 2.6 | 1.5 | 44 | 0.034091
15 | 7 | 2.6 | 2 | 59 | 0.033898
15 | 7 | 2.6 | 2.5 | 73 | 0.034247
15 | 7 | 2.6 | 3 | 88 | 0.034091
15 | 7 | 2.8 | 0.5 | 15 | 0.033333
15 | 7 | 2.8 | 1 | 30 | 0.033333
15 | 7 | 2.8 | 1.5 | 45 | 0.033333
15 | 7 | 2.8 | 2 | 59 | 0.033898
15 | 7 | 2.8 | 2.5 | 74 | 0.033784
15 | 7 | 2.8 | 3 | 89 | 0.033708
15 | 7 | 3 | 0.5 | 15 | 0.033333
15 | 7 | 3 | 1 | 30 | 0.033333
15 | 7 | 3 | 1.5 | 46 | 0.032609
15 | 7 | 3 | 2 | 61 | 0.032787
15 | 7 | 3 | 2.5 | 76 | 0.032895
15 | 7 | 3 | 3 | 91 | 0.032967
15 | 7.5 | 0.4 | 0.5 | 14 | 0.035714
15 | 7.5 | 0.4 | 1 | 28 | 0.035714
15 | 7.5 | 0.4 | 1.5 | 42 | 0.035714
15 | 7.5 | 0.4 | 2 | 55 | 0.036364
15 | 7.5 | 0.4 | 2.5 | 69 | 0.036232
15 | 7.5 | 0.4 | 3 | 83 | 0.036145
15 | 7.5 | 0.6 | 0.5 | 14 | 0.035714
15 | 7.5 | 0.6 | 1 | 29 | 0.034483
15 | 7.5 | 0.6 | 1.5 | 43 | 0.034884
15 | 7.5 | 0.6 | 2 | 57 | 0.035088
15 | 7.5 | 0.6 | 2.5 | 72 | 0.034722
15 | 7.5 | 0.6 | 3 | 86 | 0.034884
15 | 7.5 | 0.8 | 0.5 | 15 | 0.033333
15 | 7.5 | 0.8 | 1 | 29 | 0.034483
15 | 7.5 | 0.8 | 1.5 | 44 | 0.034091
15 | 7.5 | 0.8 | 2 | 59 | 0.033898
15 | 7.5 | 0.8 | 2.5 | 73 | 0.034247
15 | 7.5 | 0.8 | 3 | 88 | 0.034091
15 | 7.5 | 1 | 0.5 | 15 | 0.033333
15 | 7.5 | 1 | 1 | 30 | 0.033333
15 | 7.5 | 1 | 1.5 | 45 | 0.033333
15 | 7.5 | 1 | 2 | 60 | 0.033333
15 | 7.5 | 1 | 2.5 | 75 | 0.033333
15 | 7.5 | 1 | 3 | 90 | 0.033333
15 | 7.5 | 1.2 | 0.5 | 15 | 0.033333
15 | 7.5 | 1.2 | 1 | 31 | 0.032258
15 | 7.5 | 1.2 | 1.5 | 46 | 0.032609
15 | 7.5 | 1.2 | 2 | 61 | 0.032787
15 | 7.5 | 1.2 | 2.5 | 77 | 0.032468
15 | 7.5 | 1.2 | 3 | 92 | 0.032609
15 | 7.5 | 1.4 | 0.5 | 16 | 0.03125
15 | 7.5 | 1.4 | 1 | 31 | 0.032258
15 | 7.5 | 1.4 | 1.5 | 47 | 0.031915
15 | 7.5 | 1.4 | 2 | 63 | 0.031746
15 | 7.5 | 1.4 | 2.5 | 78 | 0.032051
15 | 7.5 | 1.4 | 3 | 94 | 0.031915
15 | 7.5 | 1.6 | 0.5 | 16 | 0.03125
15 | 7.5 | 1.6 | 1 | 32 | 0.03125
15 | 7.5 | 1.6 | 1.5 | 48 | 0.03125
15 | 7.5 | 1.6 | 2 | 64 | 0.03125
15 | 7.5 | 1.6 | 2.5 | 80 | 0.03125
15 | 7.5 | 1.6 | 3 | 96 | 0.03125
15 | 7.5 | 1.8 | 0.5 | 16 | 0.03125
15 | 7.5 | 1.8 | 1 | 33 | 0.030303
15 | 7.5 | 1.8 | 1.5 | 49 | 0.030612
15 | 7.5 | 1.8 | 2 | 65 | 0.030769
15 | 7.5 | 1.8 | 2.5 | 82 | 0.030488
15 | 7.5 | 1.8 | 3 | 98 | 0.030612
15 | 7.5 | 2 | 0.5 | 17 | 0.029412
15 | 7.5 | 2 | 1 | 33 | 0.030303
15 | 7.5 | 2 | 1.5 | 50 | 0.03
15 | 7.5 | 2 | 2 | 67 | 0.029851
15 | 7.5 | 2 | 2.5 | 83 | 0.03012
15 | 7.5 | 2 | 3 | 100 | 0.03
15 | 7.5 | 2.2 | 0.5 | 17 | 0.029412
15 | 7.5 | 2.2 | 1 | 34 | 0.029412
15 | 7.5 | 2.2 | 1.5 | 51 | 0.029412
15 | 7.5 | 2.2 | 2 | 68 | 0.029412
15 | 7.5 | 2.2 | 2.5 | 85 | 0.029412
15 | 7.5 | 2.2 | 3 | 102 | 0.029412
15 | 7.5 | 2.4 | 0.5 | 18 | 0.027778
15 | 7.5 | 2.4 | 1 | 35 | 0.028571
15 | 7.5 | 2.4 | 1.5 | 53 | 0.028302
15 | 7.5 | 2.4 | 2 | 70 | 0.028571
15 | 7.5 | 2.4 | 2.5 | 88 | 0.028409
15 | 7.5 | 2.4 | 3 | 105 | 0.028571
15 | 7.5 | 2.6 | 0.5 | 18 | 0.027778
15 | 7.5 | 2.6 | 1 | 36 | 0.027778
15 | 7.5 | 2.6 | 1.5 | 54 | 0.027778
15 | 7.5 | 2.6 | 2 | 71 | 0.028169
15 | 7.5 | 2.6 | 2.5 | 89 | 0.02809
15 | 7.5 | 2.6 | 3 | 107 | 0.028037
15 | 7.5 | 2.8 | 0.5 | 18 | 0.027778
15 | 7.5 | 2.8 | 1 | 36 | 0.027778
15 | 7.5 | 2.8 | 1.5 | 55 | 0.027273
15 | 7.5 | 2.8 | 2 | 73 | 0.027397
15 | 7.5 | 2.8 | 2.5 | 91 | 0.027473
15 | 7.5 | 2.8 | 3 | 109 | 0.027523
15 | 7.5 | 3 | 0.5 | 19 | 0.026316
15 | 7.5 | 3 | 1 | 37 | 0.027027
15 | 7.5 | 3 | 1.5 | 56 | 0.026786
15 | 7.5 | 3 | 2 | 74 | 0.027027
15 | 7.5 | 3 | 2.5 | 93 | 0.026882
15 | 7.5 | 3 | 3 | 111 | 0.027027
15 | 8 | 0.4 | 0.5 | 17 | 0.029412
15 | 8 | 0.4 | 1 | 33 | 0.030303
15 | 8 | 0.4 | 1.5 | 50 | 0.03
15 | 8 | 0.4 | 2 | 66 | 0.030303
15 | 8 | 0.4 | 2.5 | 83 | 0.03012
15 | 8 | 0.4 | 3 | 99 | 0.030303
15 | 8 | 0.6 | 0.5 | 17 | 0.029412
15 | 8 | 0.6 | 1 | 34 | 0.029412
15 | 8 | 0.6 | 1.5 | 51 | 0.029412
15 | 8 | 0.6 | 2 | 68 | 0.029412
15 | 8 | 0.6 | 2.5 | 85 | 0.029412
15 | 8 | 0.6 | 3 | 102 | 0.029412
15 | 8 | 0.8 | 0.5 | 18 | 0.027778
15 | 8 | 0.8 | 1 | 35 | 0.028571
15 | 8 | 0.8 | 1.5 | 53 | 0.028302
15 | 8 | 0.8 | 2 | 70 | 0.028571
15 | 8 | 0.8 | 2.5 | 88 | 0.028409
15 | 8 | 0.8 | 3 | 105 | 0.028571
15 | 8 | 1 | 0.5 | 18 | 0.027778
15 | 8 | 1 | 1 | 36 | 0.027778
15 | 8 | 1 | 1.5 | 54 | 0.027778
15 | 8 | 1 | 2 | 72 | 0.027778
15 | 8 | 1 | 2.5 | 90 | 0.027778
15 | 8 | 1 | 3 | 108 | 0.027778
15 | 8 | 1.2 | 0.5 | 19 | 0.026316
15 | 8 | 1.2 | 1 | 37 | 0.027027
15 | 8 | 1.2 | 1.5 | 57 | 0.026316
15 | 8 | 1.2 | 2 | 74 | 0.027027
15 | 8 | 1.2 | 2.5 | 93 | 0.026882
15 | 8 | 1.2 | 3 | 111 | 0.027027
15 | 8 | 1.4 | 0.5 | 19 | 0.026316
15 | 8 | 1.4 | 1 | 38 | 0.026316
15 | 8 | 1.4 | 1.5 | 57 | 0.026316
15 | 8 | 1.4 | 2 | 76 | 0.026316
15 | 8 | 1.4 | 2.5 | 95 | 0.026316
15 | 8 | 1.4 | 3 | 114 | 0.026316
15 | 8 | 1.6 | 0.5 | 19 | 0.026316
15 | 8 | 1.6 | 1 | 39 | 0.025641
15 | 8 | 1.6 | 1.5 | 58 | 0.025862
15 | 8 | 1.6 | 2 | 77 | 0.025974
15 | 8 | 1.6 | 2.5 | 97 | 0.025773
15 | 8 | 1.6 | 3 | 116 | 0.025862
15 | 8 | 1.8 | 0.5 | 20 | 0.025
15 | 8 | 1.8 | 1 | 40 | 0.025
15 | 8 | 1.8 | 1.5 | 60 | 0.025
15 | 8 | 1.8 | 2 | 79 | 0.025316
15 | 8 | 1.8 | 2.5 | 99 | 0.025253
15 | 8 | 1.8 | 3 | 119 | 0.02521
15 | 8 | 2 | 0.5 | 20 | 0.025
15 | 8 | 2 | 1 | 41 | 0.02439
15 | 8 | 2 | 1.5 | 61 | 0.02459
15 | 8 | 2 | 2 | 81 | 0.024691
15 | 8 | 2 | 2.5 | 102 | 0.02451
15 | 8 | 2 | 3 | 122 | 0.02459
15 | 8 | 2.2 | 0.5 | 21 | 0.02381
15 | 8 | 2.2 | 1 | 41 | 0.02439
15 | 8 | 2.2 | 1.5 | 62 | 0.024194
15 | 8 | 2.2 | 2 | 83 | 0.024096
15 | 8 | 2.2 | 2.5 | 103 | 0.024272
15 | 8 | 2.2 | 3 | 124 | 0.024194
15 | 8 | 2.4 | 0.5 | 21 | 0.02381
15 | 8 | 2.4 | 1 | 42 | 0.02381
15 | 8 | 2.4 | 1.5 | 64 | 0.023438
15 | 8 | 2.4 | 2 | 85 | 0.023529
15 | 8 | 2.4 | 2.5 | 106 | 0.023585
15 | 8 | 2.4 | 3 | 127 | 0.023622
15 | 8 | 2.6 | 0.5 | 22 | 0.022727
15 | 8 | 2.6 | 1 | 43 | 0.023256
15 | 8 | 2.6 | 1.5 | 65 | 0.023077
15 | 8 | 2.6 | 2 | 86 | 0.023256
15 | 8 | 2.6 | 2.5 | 108 | 0.023148
15 | 8 | 2.6 | 3 | 129 | 0.023256
15 | 8 | 2.8 | 0.5 | 22 | 0.022727
15 | 8 | 2.8 | 1 | 44 | 0.022727
15 | 8 | 2.8 | 1.5 | 66 | 0.022727
15 | 8 | 2.8 | 2 | 88 | 0.022727
15 | 8 | 2.8 | 2.5 | 110 | 0.022727
15 | 8 | 2.8 | 3 | 132 | 0.022727
15 | 8 | 3 | 0.5 | 22 | 0.022727
15 | 8 | 3 | 1 | 45 | 0.022222
15 | 8 | 3 | 1.5 | 67 | 0.022388
15 | 8 | 3 | 2 | 89 | 0.022472
15 | 8 | 3 | 2.5 | 112 | 0.022321
15 | 8 | 3 | 3 | 134 | 0.022388
15 | 8.5 | 0.4 | 0.5 | 20 | 0.025
15 | 8.5 | 0.4 | 1 | 39 | 0.025641
15 | 8.5 | 0.4 | 1.5 | 59 | 0.025424
15 | 8.5 | 0.4 | 2 | 79 | 0.025316
15 | 8.5 | 0.4 | 2.5 | 98 | 0.02551
15 | 8.5 | 0.4 | 3 | 118 | 0.025424
15 | 8.5 | 0.6 | 0.5 | 20 | 0.025
15 | 8.5 | 0.6 | 1 | 41 | 0.02439
15 | 8.5 | 0.6 | 1.5 | 61 | 0.02459
15 | 8.5 | 0.6 | 2 | 81 | 0.024691
15 | 8.5 | 0.6 | 2.5 | 102 | 0.02451
15 | 8.5 | 0.6 | 3 | 122 | 0.02459
15 | 8.5 | 0.8 | 0.5 | 21 | 0.02381
15 | 8.5 | 0.8 | 1 | 42 | 0.02381
15 | 8.5 | 0.8 | 1.5 | 63 | 0.02381
15 | 8.5 | 0.8 | 2 | 84 | 0.02381
15 | 8.5 | 0.8 | 2.5 | 105 | 0.02381
15 | 8.5 | 0.8 | 3 | 126 | 0.02381
15 | 8.5 | 1 | 0.5 | 22 | 0.022727
15 | 8.5 | 1 | 1 | 43 | 0.023256
15 | 8.5 | 1 | 1.5 | 65 | 0.023077
15 | 8.5 | 1 | 2 | 87 | 0.022989
15 | 8.5 | 1 | 2.5 | 108 | 0.023148
15 | 8.5 | 1 | 3 | 130 | 0.023077
15 | 8.5 | 1.2 | 0.5 | 22 | 0.022727
15 | 8.5 | 1.2 | 1 | 45 | 0.022222
15 | 8.5 | 1.2 | 1.5 | 67 | 0.022388
15 | 8.5 | 1.2 | 2 | 89 | 0.022472
15 | 8.5 | 1.2 | 2.5 | 112 | 0.022321
15 | 8.5 | 1.2 | 3 | 134 | 0.022388
15 | 8.5 | 1.4 | 0.5 | 23 | 0.021739
15 | 8.5 | 1.4 | 1 | 46 | 0.021739
15 | 8.5 | 1.4 | 1.5 | 69 | 0.021739
15 | 8.5 | 1.4 | 2 | 91 | 0.021978
15 | 8.5 | 1.4 | 2.5 | 114 | 0.02193
15 | 8.5 | 1.4 | 3 | 137 | 0.021898
15 | 8.5 | 1.6 | 0.5 | 24 | 0.020833
15 | 8.5 | 1.6 | 1 | 47 | 0.021277
15 | 8.5 | 1.6 | 1.5 | 71 | 0.021127
15 | 8.5 | 1.6 | 2 | 94 | 0.021277
15 | 8.5 | 1.6 | 2.5 | 118 | 0.021186
15 | 8.5 | 1.6 | 3 | 141 | 0.021277
15 | 8.5 | 1.8 | 0.5 | 24 | 0.020833
15 | 8.5 | 1.8 | 1 | 48 | 0.020833
15 | 8.5 | 1.8 | 1.5 | 72 | 0.020833
15 | 8.5 | 1.8 | 2 | 93 | 0.021505
15 | 8.5 | 1.8 | 2.5 | 120 | 0.020833
15 | 8.5 | 1.8 | 3 | 144 | 0.020833
15 | 8.5 | 2 | 0.5 | 25 | 0.02
15 | 8.5 | 2 | 1 | 49 | 0.020408
15 | 8.5 | 2 | 1.5 | 74 | 0.02027
15 | 8.5 | 2 | 2 | 98 | 0.020408
15 | 8.5 | 2 | 2.5 | 123 | 0.020325
15 | 8.5 | 2 | 3 | 147 | 0.020408
15 | 8.5 | 2.2 | 0.5 | 25 | 0.02
15 | 8.5 | 2.2 | 1 | 50 | 0.02
15 | 8.5 | 2.2 | 1.5 | 75 | 0.02
15 | 8.5 | 2.2 | 2 | 100 | 0.02
15 | 8.5 | 2.2 | 2.5 | 125 | 0.02
15 | 8.5 | 2.2 | 3 | 150 | 0.02
15 | 8.5 | 2.4 | 0.5 | 26 | 0.019231
15 | 8.5 | 2.4 | 1 | 51 | 0.019608
15 | 8.5 | 2.4 | 1.5 | 77 | 0.019481
15 | 8.5 | 2.4 | 2 | 102 | 0.019608
15 | 8.5 | 2.4 | 2.5 | 128 | 0.019531
15 | 8.5 | 2.4 | 3 | 153 | 0.019608
15 | 8.5 | 2.6 | 0.5 | 26 | 0.019231
15 | 8.5 | 2.6 | 1 | 52 | 0.019231
15 | 8.5 | 2.6 | 1.5 | 78 | 0.019231
15 | 8.5 | 2.6 | 2 | 104 | 0.019231
15 | 8.5 | 2.6 | 2.5 | 130 | 0.019231
15 | 8.5 | 2.6 | 3 | 156 | 0.019231
15 | 8.5 | 2.8 | 0.5 | 27 | 0.018519
15 | 8.5 | 2.8 | 1 | 53 | 0.018868
15 | 8.5 | 2.8 | 1.5 | 80 | 0.01875
15 | 8.5 | 2.8 | 2 | 106 | 0.018868
15 | 8.5 | 2.8 | 2.5 | 133 | 0.018797
15 | 8.5 | 2.8 | 3 | 159 | 0.018868
15 | 8.5 | 3 | 0.5 | 27 | 0.018519
15 | 8.5 | 3 | 1 | 54 | 0.018519
15 | 8.5 | 3 | 1.5 | 81 | 0.018519
15 | 8.5 | 3 | 2 | 108 | 0.018519
15 | 8.5 | 3 | 2.5 | 135 | 0.018519
15 | 8.5 | 3 | 3 | 162 | 0.018519
20 | 7 | 0.4 | 0.5 | 9 | 0.055556
20 | 7 | 0.4 | 1 | 17 | 0.058824
20 | 7 | 0.4 | 1.5 | 26 | 0.057692
20 | 7 | 0.4 | 2 | 35 | 0.057143
20 | 7 | 0.4 | 2.5 | 43 | 0.05814
20 | 7 | 0.4 | 3 | 52 | 0.057692
20 | 7 | 0.6 | 0.5 | 9 | 0.055556
20 | 7 | 0.6 | 1 | 18 | 0.055556
20 | 7 | 0.6 | 1.5 | 27 | 0.055556
20 | 7 | 0.6 | 2 | 36 | 0.055556
20 | 7 | 0.6 | 2.5 | 45 | 0.055556
20 | 7 | 0.6 | 3 | 54 | 0.055556
20 | 7 | 0.8 | 0.5 | 9 | 0.055556
20 | 7 | 0.8 | 1 | 18 | 0.055556
20 | 7 | 0.8 | 1.5 | 28 | 0.053571
20 | 7 | 0.8 | 2 | 37 | 0.054054
20 | 7 | 0.8 | 2.5 | 46 | 0.054348
20 | 7 | 0.8 | 3 | 55 | 0.054545
20 | 7 | 1 | 0.5 | 9 | 0.055556
20 | 7 | 1 | 1 | 19 | 0.052632
20 | 7 | 1 | 1.5 | 28 | 0.053571
20 | 7 | 1 | 2 | 37 | 0.054054
20 | 7 | 1 | 2.5 | 47 | 0.053191
20 | 7 | 1 | 3 | 56 | 0.053571
20 | 7 | 1.2 | 0.5 | 10 | 0.05
20 | 7 | 1.2 | 1 | 19 | 0.052632
20 | 7 | 1.2 | 1.5 | 29 | 0.051724
20 | 7 | 1.2 | 2 | 38 | 0.052632
20 | 7 | 1.2 | 2.5 | 48 | 0.052083
20 | 7 | 1.2 | 3 | 57 | 0.052632
20 | 7 | 1.4 | 0.5 | 10 | 0.05
20 | 7 | 1.4 | 1 | 19 | 0.052632
20 | 7 | 1.4 | 1.5 | 29 | 0.051724
20 | 7 | 1.4 | 2 | 39 | 0.051282
20 | 7 | 1.4 | 2.5 | 48 | 0.052083
20 | 7 | 1.4 | 3 | 58 | 0.051724
20 | 7 | 1.6 | 0.5 | 10 | 0.05
20 | 7 | 1.6 | 1 | 20 | 0.05
20 | 7 | 1.6 | 1.5 | 30 | 0.05
20 | 7 | 1.6 | 2 | 39 | 0.051282
20 | 7 | 1.6 | 2.5 | 49 | 0.05102
20 | 7 | 1.6 | 3 | 59 | 0.050847
20 | 7 | 1.8 | 0.5 | 10 | 0.05
20 | 7 | 1.8 | 1 | 20 | 0.05
20 | 7 | 1.8 | 1.5 | 31 | 0.048387
20 | 7 | 1.8 | 2 | 41 | 0.04878
20 | 7 | 1.8 | 2.5 | 51 | 0.04902
20 | 7 | 1.8 | 3 | 61 | 0.04918
20 | 7 | 2 | 0.5 | 10 | 0.05
20 | 7 | 2 | 1 | 21 | 0.047619
20 | 7 | 2 | 1.5 | 31 | 0.048387
20 | 7 | 2 | 2 | 41 | 0.04878
20 | 7 | 2 | 2.5 | 52 | 0.048077
20 | 7 | 2 | 3 | 62 | 0.048387
20 | 7 | 2.2 | 0.5 | 11 | 0.045455
20 | 7 | 2.2 | 1 | 21 | 0.047619
20 | 7 | 2.2 | 1.5 | 32 | 0.046875
20 | 7 | 2.2 | 2 | 42 | 0.047619
20 | 7 | 2.2 | 2.5 | 53 | 0.04717
20 | 7 | 2.2 | 3 | 63 | 0.047619
20 | 7 | 2.4 | 0.5 | 11 | 0.045455
20 | 7 | 2.4 | 1 | 22 | 0.045455
20 | 7 | 2.4 | 1.5 | 33 | 0.045455
20 | 7 | 2.4 | 2 | 43 | 0.046512
20 | 7 | 2.4 | 2.5 | 54 | 0.046296
20 | 7 | 2.4 | 3 | 65 | 0.046154
20 | 7 | 2.6 | 0.5 | 11 | 0.045455
20 | 7 | 2.6 | 1 | 22 | 0.045455
20 | 7 | 2.6 | 1.5 | 33 | 0.045455
20 | 7 | 2.6 | 2 | 44 | 0.045455
20 | 7 | 2.6 | 2.5 | 55 | 0.045455
20 | 7 | 2.6 | 3 | 66 | 0.045455
20 | 7 | 2.8 | 0.5 | 11 | 0.045455
20 | 7 | 2.8 | 1 | 22 | 0.045455
20 | 7 | 2.8 | 1.5 | 34 | 0.044118
20 | 7 | 2.8 | 2 | 45 | 0.044444
20 | 7 | 2.8 | 2.5 | 56 | 0.044643
20 | 7 | 2.8 | 3 | 67 | 0.044776
20 | 7 | 3 | 0.5 | 11 | 0.045455
20 | 7 | 3 | 1 | 23 | 0.043478
20 | 7 | 3 | 1.5 | 34 | 0.044118
20 | 7 | 3 | 2 | 45 | 0.044444
20 | 7 | 3 | 2.5 | 57 | 0.04386
20 | 7 | 3 | 3 | 68 | 0.044118
20 | 7.5 | 0.4 | 0.5 | 10 | 0.05
20 | 7.5 | 0.4 | 1 | 21 | 0.047619
20 | 7.5 | 0.4 | 1.5 | 31 | 0.048387
20 | 7.5 | 0.4 | 2 | 41 | 0.04878
20 | 7.5 | 0.4 | 2.5 | 52 | 0.048077
20 | 7.5 | 0.4 | 3 | 62 | 0.048387
20 | 7.5 | 0.6 | 0.5 | 11 | 0.045455
20 | 7.5 | 0.6 | 1 | 21 | 0.047619
20 | 7.5 | 0.6 | 1.5 | 32 | 0.046875
20 | 7.5 | 0.6 | 2 | 43 | 0.046512
20 | 7.5 | 0.6 | 2.5 | 53 | 0.04717
20 | 7.5 | 0.6 | 3 | 64 | 0.046875
20 | 7.5 | 0.8 | 0.5 | 11 | 0.045455
20 | 7.5 | 0.8 | 1 | 22 | 0.045455
20 | 7.5 | 0.8 | 1.5 | 33 | 0.045455
20 | 7.5 | 0.8 | 2 | 44 | 0.045455
20 | 7.5 | 0.8 | 2.5 | 55 | 0.045455
20 | 7.5 | 0.8 | 3 | 66 | 0.045455
20 | 7.5 | 1 | 0.5 | 11 | 0.045455
20 | 7.5 | 1 | 1 | 22 | 0.045455
20 | 7.5 | 1 | 1.5 | 34 | 0.044118
20 | 7.5 | 1 | 2 | 45 | 0.044444
20 | 7.5 | 1 | 2.5 | 56 | 0.044643
20 | 7.5 | 1 | 3 | 67 | 0.044776
20 | 7.5 | 1.2 | 0.5 | 12 | 0.041667
20 | 7.5 | 1.2 | 1 | 23 | 0.043478
20 | 7.5 | 1.2 | 1.5 | 35 | 0.042857
20 | 7.5 | 1.2 | 2 | 46 | 0.043478
20 | 7.5 | 1.2 | 2.5 | 58 | 0.043103
20 | 7.5 | 1.2 | 3 | 69 | 0.043478
20 | 7.5 | 1.4 | 0.5 | 12 | 0.041667
20 | 7.5 | 1.4 | 1 | 23 | 0.043478
20 | 7.5 | 1.4 | 1.5 | 35 | 0.042857
20 | 7.5 | 1.4 | 2 | 47 | 0.042553
20 | 7.5 | 1.4 | 2.5 | 58 | 0.043103
20 | 7.5 | 1.4 | 3 | 70 | 0.042857
20 | 7.5 | 1.6 | 0.5 | 12 | 0.041667
20 | 7.5 | 1.6 | 1 | 24 | 0.041667
20 | 7.5 | 1.6 | 1.5 | 36 | 0.041667
20 | 7.5 | 1.6 | 2 | 48 | 0.041667
20 | 7.5 | 1.6 | 2.5 | 60 | 0.041667
20 | 7.5 | 1.6 | 3 | 72 | 0.041667
20 | 7.5 | 1.8 | 0.5 | 12 | 0.041667
20 | 7.5 | 1.8 | 1 | 25 | 0.04
20 | 7.5 | 1.8 | 1.5 | 37 | 0.040541
20 | 7.5 | 1.8 | 2 | 49 | 0.040816
20 | 7.5 | 1.8 | 2.5 | 62 | 0.040323
20 | 7.5 | 1.8 | 3 | 74 | 0.040541
20 | 7.5 | 2 | 0.5 | 13 | 0.038462
20 | 7.5 | 2 | 1 | 25 | 0.04
20 | 7.5 | 2 | 1.5 | 38 | 0.039474
20 | 7.5 | 2 | 2 | 50 | 0.04
20 | 7.5 | 2 | 2.5 | 63 | 0.039683
20 | 7.5 | 2 | 3 | 75 | 0.04
20 | 7.5 | 2.2 | 0.5 | 13 | 0.038462
20 | 7.5 | 2.2 | 1 | 26 | 0.038462
20 | 7.5 | 2.2 | 1.5 | 39 | 0.038462
20 | 7.5 | 2.2 | 2 | 51 | 0.039216
20 | 7.5 | 2.2 | 2.5 | 64 | 0.039062
20 | 7.5 | 2.2 | 3 | 77 | 0.038961
20 | 7.5 | 2.4 | 0.5 | 13 | 0.038462
20 | 7.5 | 2.4 | 1 | 26 | 0.038462
20 | 7.5 | 2.4 | 1.5 | 39 | 0.038462
20 | 7.5 | 2.4 | 2 | 52 | 0.038462
20 | 7.5 | 2.4 | 2.5 | 65 | 0.038462
20 | 7.5 | 2.4 | 3 | 78 | 0.038462
20 | 7.5 | 2.6 | 0.5 | 13 | 0.038462
20 | 7.5 | 2.6 | 1 | 27 | 0.037037
20 | 7.5 | 2.6 | 1.5 | 40 | 0.0375
20 | 7.5 | 2.6 | 2 | 53 | 0.037736
20 | 7.5 | 2.6 | 2.5 | 67 | 0.037313
20 | 7.5 | 2.6 | 3 | 80 | 0.0375
20 | 7.5 | 2.8 | 0.5 | 14 | 0.035714
20 | 7.5 | 2.8 | 1 | 27 | 0.037037
20 | 7.5 | 2.8 | 1.5 | 41 | 0.036585
20 | 7.5 | 2.8 | 2 | 54 | 0.037037
20 | 7.5 | 2.8 | 2.5 | 68 | 0.036765
20 | 7.5 | 2.8 | 3 | 81 | 0.037037
20 | 7.5 | 3 | 0.5 | 14 | 0.035714
20 | 7.5 | 3 | 1 | 28 | 0.035714
20 | 7.5 | 3 | 1.5 | 42 | 0.035714
20 | 7.5 | 3 | 2 | 55 | 0.036364
20 | 7.5 | 3 | 2.5 | 69 | 0.036232
20 | 7.5 | 3 | 3 | 83 | 0.036145
20 | 8 | 0.4 | 0.5 | 12 | 0.041667
20 | 8 | 0.4 | 1 | 25 | 0.04
20 | 8 | 0.4 | 1.5 | 37 | 0.040541
20 | 8 | 0.4 | 2 | 49 | 0.040816
20 | 8 | 0.4 | 2.5 | 62 | 0.040323
20 | 8 | 0.4 | 3 | 74 | 0.040541
20 | 8 | 0.6 | 0.5 | 13 | 0.038462
20 | 8 | 0.6 | 1 | 26 | 0.038462
20 | 8 | 0.6 | 1.5 | 39 | 0.038462
20 | 8 | 0.6 | 2 | 51 | 0.039216
20 | 8 | 0.6 | 2.5 | 64 | 0.039062
20 | 8 | 0.6 | 3 | 77 | 0.038961
20 | 8 | 0.8 | 0.5 | 13 | 0.038462
20 | 8 | 0.8 | 1 | 26 | 0.038462
20 | 8 | 0.8 | 1.5 | 40 | 0.0375
20 | 8 | 0.8 | 2 | 53 | 0.037736
20 | 8 | 0.8 | 2.5 | 66 | 0.037879
20 | 8 | 0.8 | 3 | 79 | 0.037975
20 | 8 | 1 | 0.5 | 14 | 0.035714
20 | 8 | 1 | 1 | 27 | 0.037037
20 | 8 | 1 | 1.5 | 41 | 0.036585
20 | 8 | 1 | 2 | 54 | 0.037037
20 | 8 | 1 | 2.5 | 68 | 0.036765
20 | 8 | 1 | 3 | 81 | 0.037037
20 | 8 | 1.2 | 0.5 | 14 | 0.035714
20 | 8 | 1.2 | 1 | 28 | 0.035714
20 | 8 | 1.2 | 1.5 | 42 | 0.035714
20 | 8 | 1.2 | 2 | 55 | 0.036364
20 | 8 | 1.2 | 2.5 | 69 | 0.036232
20 | 8 | 1.2 | 3 | 83 | 0.036145
20 | 8 | 1.4 | 0.5 | 14 | 0.035714
20 | 8 | 1.4 | 1 | 28 | 0.035714
20 | 8 | 1.4 | 1.5 | 43 | 0.034884
20 | 8 | 1.4 | 2 | 57 | 0.035088
20 | 8 | 1.4 | 2.5 | 71 | 0.035211
20 | 8 | 1.4 | 3 | 85 | 0.035294
20 | 8 | 1.6 | 0.5 | 15 | 0.033333
20 | 8 | 1.6 | 1 | 29 | 0.034483
20 | 8 | 1.6 | 1.5 | 44 | 0.034091
20 | 8 | 1.6 | 2 | 58 | 0.034483
20 | 8 | 1.6 | 2.5 | 73 | 0.034247
20 | 8 | 1.6 | 3 | 87 | 0.034483
20 | 8 | 1.8 | 0.5 | 15 | 0.033333
20 | 8 | 1.8 | 1 | 30 | 0.033333
20 | 8 | 1.8 | 1.5 | 45 | 0.033333
20 | 8 | 1.8 | 2 | 59 | 0.033898
20 | 8 | 1.8 | 2.5 | 74 | 0.033784
20 | 8 | 1.8 | 3 | 89 | 0.033708
20 | 8 | 2 | 0.5 | 15 | 0.033333
20 | 8 | 2 | 1 | 30 | 0.033333
20 | 8 | 2 | 1.5 | 46 | 0.032609
20 | 8 | 2 | 2 | 61 | 0.032787
20 | 8 | 2 | 2.5 | 76 | 0.032895
20 | 8 | 2 | 3 | 91 | 0.032967
20 | 8 | 2.2 | 0.5 | 16 | 0.03125
20 | 8 | 2.2 | 1 | 31 | 0.032258
20 | 8 | 2.2 | 1.5 | 47 | 0.031915
20 | 8 | 2.2 | 2 | 62 | 0.032258
20 | 8 | 2.2 | 2.5 | 78 | 0.032051
20 | 8 | 2.2 | 3 | 93 | 0.032258
20 | 8 | 2.4 | 0.5 | 16 | 0.03125
20 | 8 | 2.4 | 1 | 32 | 0.03125
20 | 8 | 2.4 | 1.5 | 48 | 0.03125
20 | 8 | 2.4 | 2 | 63 | 0.031746
20 | 8 | 2.4 | 2.5 | 79 | 0.031646
20 | 8 | 2.4 | 3 | 95 | 0.031579
20 | 8 | 2.6 | 0.5 | 16 | 0.03125
20 | 8 | 2.6 | 1 | 32 | 0.03125
20 | 8 | 2.6 | 1.5 | 49 | 0.030612
20 | 8 | 2.6 | 2 | 65 | 0.030769
20 | 8 | 2.6 | 2.5 | 81 | 0.030864
20 | 8 | 2.6 | 3 | 97 | 0.030928
20 | 8 | 2.8 | 0.5 | 17 | 0.029412
20 | 8 | 2.8 | 1 | 33 | 0.030303
20 | 8 | 2.8 | 1.5 | 50 | 0.03
20 | 8 | 2.8 | 2 | 66 | 0.030303
20 | 8 | 2.8 | 2.5 | 83 | 0.03012
20 | 8 | 2.8 | 3 | 99 | 0.030303
20 | 8 | 3 | 0.5 | 17 | 0.029412
20 | 8 | 3 | 1 | 34 | 0.029412
20 | 8 | 3 | 1.5 | 51 | 0.029412
20 | 8 | 3 | 2 | 67 | 0.029851
20 | 8 | 3 | 2.5 | 84 | 0.029762
20 | 8 | 3 | 3 | 101 | 0.029703
20 | 8.5 | 0.4 | 0.5 | 15 | 0.033333
20 | 8.5 | 0.4 | 1 | 30 | 0.033333
20 | 8.5 | 0.4 | 1.5 | 45 | 0.033333
20 | 8.5 | 0.4 | 2 | 59 | 0.033898
20 | 8.5 | 0.4 | 2.5 | 74 | 0.033784
20 | 8.5 | 0.4 | 3 | 89 | 0.033708
20 | 8.5 | 0.6 | 0.5 | 15 | 0.033333
20 | 8.5 | 0.6 | 1 | 31 | 0.032258
20 | 8.5 | 0.6 | 1.5 | 46 | 0.032609
20 | 8.5 | 0.6 | 2 | 61 | 0.032787
20 | 8.5 | 0.6 | 2.5 | 77 | 0.032468
20 | 8.5 | 0.6 | 3 | 92 | 0.032609
20 | 8.5 | 0.8 | 0.5 | 16 | 0.03125
20 | 8.5 | 0.8 | 1 | 32 | 0.03125
20 | 8.5 | 0.8 | 1.5 | 48 | 0.03125
20 | 8.5 | 0.8 | 2 | 63 | 0.031746
20 | 8.5 | 0.8 | 2.5 | 79 | 0.031646
20 | 8.5 | 0.8 | 3 | 95 | 0.031579
20 | 8.5 | 1 | 0.5 | 16 | 0.03125
20 | 8.5 | 1 | 1 | 33 | 0.030303
20 | 8.5 | 1 | 1.5 | 49 | 0.030612
20 | 8.5 | 1 | 2 | 65 | 0.030769
20 | 8.5 | 1 | 2.5 | 82 | 0.030488
20 | 8.5 | 1 | 3 | 98 | 0.030612
20 | 8.5 | 1.2 | 0.5 | 17 | 0.029412
20 | 8.5 | 1.2 | 1 | 33 | 0.030303
20 | 8.5 | 1.2 | 1.5 | 50 | 0.03
20 | 8.5 | 1.2 | 2 | 67 | 0.029851
20 | 8.5 | 1.2 | 2.5 | 83 | 0.03012
20 | 8.5 | 1.2 | 3 | 100 | 0.03
20 | 8.5 | 1.4 | 0.5 | 17 | 0.029412
20 | 8.5 | 1.4 | 1 | 34 | 0.029412
20 | 8.5 | 1.4 | 1.5 | 52 | 0.028846
20 | 8.5 | 1.4 | 2 | 69 | 0.028986
20 | 8.5 | 1.4 | 2.5 | 86 | 0.02907
20 | 8.5 | 1.4 | 3 | 103 | 0.029126
20 | 8.5 | 1.6 | 0.5 | 18 | 0.027778
20 | 8.5 | 1.6 | 1 | 35 | 0.028571
20 | 8.5 | 1.6 | 1.5 | 53 | 0.028302
20 | 8.5 | 1.6 | 2 | 70 | 0.028571
20 | 8.5 | 1.6 | 2.5 | 88 | 0.028409
20 | 8.5 | 1.6 | 3 | 105 | 0.028571
20 | 8.5 | 1.8 | 0.5 | 18 | 0.027778
20 | 8.5 | 1.8 | 1 | 36 | 0.027778
20 | 8.5 | 1.8 | 1.5 | 54 | 0.027778
20 | 8.5 | 1.8 | 2 | 72 | 0.027778
20 | 8.5 | 1.8 | 2.5 | 90 | 0.027778
20 | 8.5 | 1.8 | 3 | 108 | 0.027778
20 | 8.5 | 2 | 0.5 | 18 | 0.027778
20 | 8.5 | 2 | 1 | 37 | 0.027027
20 | 8.5 | 2 | 1.5 | 55 | 0.027273
20 | 8.5 | 2 | 2 | 73 | 0.027397
20 | 8.5 | 2 | 2.5 | 92 | 0.027174
20 | 8.5 | 2 | 3 | 110 | 0.027273
20 | 8.5 | 2.2 | 0.5 | 19 | 0.026316
20 | 8.5 | 2.2 | 1 | 38 | 0.026316
20 | 8.5 | 2.2 | 1.5 | 57 | 0.026316
20 | 8.5 | 2.2 | 2 | 75 | 0.026667
20 | 8.5 | 2.2 | 2.5 | 94 | 0.026596
20 | 8.5 | 2.2 | 3 | 113 | 0.026549
20 | 8.5 | 2.4 | 0.5 | 20 | 0.025
20 | 8.5 | 2.4 | 1 | 39 | 0.025641
20 | 8.5 | 2.4 | 1.5 | 59 | 0.025424
20 | 8.5 | 2.4 | 2 | 78 | 0.025641
20 | 8.5 | 2.4 | 2.5 | 98 | 0.02551
20 | 8.5 | 2.4 | 3 | 115 | 0.026087
20 | 8.5 | 2.6 | 0.5 | 20 | 0.025
20 | 8.5 | 2.6 | 1 | 39 | 0.025641
20 | 8.5 | 2.6 | 1.5 | 59 | 0.025424
20 | 8.5 | 2.6 | 2 | 78 | 0.025641
20 | 8.5 | 2.6 | 2.5 | 98 | 0.02551
20 | 8.5 | 2.6 | 3 | 117 | 0.025641
20 | 8.5 | 2.8 | 0.5 | 20 | 0.025
20 | 8.5 | 2.8 | 1 | 40 | 0.025
20 | 8.5 | 2.8 | 1.5 | 60 | 0.025
20 | 8.5 | 2.8 | 2 | 79 | 0.025316
20 | 8.5 | 2.8 | 2.5 | 99 | 0.025253
20 | 8.5 | 2.8 | 3 | 119 | 0.02521
20 | 8.5 | 3 | 0.5 | 20 | 0.025
20 | 8.5 | 3 | 1 | 41 | 0.02439
20 | 8.5 | 3 | 1.5 | 61 | 0.02459
20 | 8.5 | 3 | 2 | 81 | 0.024691
20 | 8.5 | 3 | 2.5 | 102 | 0.02451
20 | 8.5 | 3 | 3 | 122 | 0.02459
0.5 | 9 | 0.4 | 0.5 | 65 | 0.0076923
0.5 | 9 | 0.4 | 1 | 130 | 0.0076923
0.5 | 9 | 0.4 | 1.5 | 195 | 0.0076923
0.5 | 9 | 0.4 | 2 | 260 | 0.0076923
0.5 | 9 | 0.4 | 2.5 | 325 | 0.0076923
0.5 | 9 | 0.4 | 3 | 390 | 0.0076923
0.5 | 9 | 0.6 | 0.5 | 68 | 0.0073529
0.5 | 9 | 0.6 | 1 | 136 | 0.0073529
0.5 | 9 | 0.6 | 1.5 | 204 | 0.0073529
0.5 | 9 | 0.6 | 2 | 271 | 0.0073801
0.5 | 9 | 0.6 | 2.5 | 339 | 0.0073746
0.5 | 9 | 0.6 | 3 | 407 | 0.007371
0.5 | 9 | 0.8 | 0.5 | 70 | 0.0071429
0.5 | 9 | 0.8 | 1 | 141 | 0.0070922
0.5 | 9 | 0.8 | 1.5 | 211 | 0.007109
0.5 | 9 | 0.8 | 2 | 281 | 0.0071174
0.5 | 9 | 0.8 | 2.5 | 352 | 0.0071023
0.5 | 9 | 0.8 | 3 | 422 | 0.007109
0.5 | 9 | 1 | 0.5 | 73 | 0.0068493
0.5 | 9 | 1 | 1 | 146 | 0.0068493
0.5 | 9 | 1 | 1.5 | 219 | 0.0068493
0.5 | 9 | 1 | 2 | 291 | 0.0068729
0.5 | 9 | 1 | 2.5 | 364 | 0.0068681
0.5 | 9 | 1 | 3 | 437 | 0.006865
0.5 | 9 | 1.2 | 0.5 | 75 | 0.0066667
0.5 | 9 | 1.2 | 1 | 150 | 0.0066667
0.5 | 9 | 1.2 | 1.5 | 226 | 0.0066372
0.5 | 9 | 1.2 | 2 | 301 | 0.0066445
0.5 | 9 | 1.2 | 2.5 | 376 | 0.0066489
0.5 | 9 | 1.2 | 3 | 451 | 0.0066519
0.5 | 9 | 1.4 | 0.5 | 77 | 0.0064935
0.5 | 9 | 1.4 | 1 | 155 | 0.0064516
0.5 | 9 | 1.4 | 1.5 | 232 | 0.0064655
0.5 | 9 | 1.4 | 2 | 309 | 0.0064725
0.5 | 9 | 1.4 | 2.5 | 387 | 0.0064599
0.5 | 9 | 1.4 | 3 | 464 | 0.0064655
0.5 | 9 | 1.6 | 0.5 | 80 | 0.00625
0.5 | 9 | 1.6 | 1 | 159 | 0.0062893
0.5 | 9 | 1.6 | 1.5 | 239 | 0.0062762
0.5 | 9 | 1.6 | 2 | 318 | 0.0062893
0.5 | 9 | 1.6 | 2.5 | 398 | 0.0062814
0.5 | 9 | 1.6 | 3 | 477 | 0.0062893
0.5 | 9 | 1.8 | 0.5 | 82 | 0.0060976
0.5 | 9 | 1.8 | 1 | 163 | 0.006135
0.5 | 9 | 1.8 | 1.5 | 245 | 0.0061224
0.5 | 9 | 1.8 | 2 | 326 | 0.006135
0.5 | 9 | 1.8 | 2.5 | 408 | 0.0061275
0.5 | 9 | 1.8 | 3 | 489 | 0.006135
0.5 | 9 | 2 | 0.5 | 83 | 0.0060241
0.5 | 9 | 2 | 1 | 167 | 0.005988
0.5 | 9 | 2 | 1.5 | 250 | 0.006
0.5 | 9 | 2 | 2 | 333 | 0.006006
0.5 | 9 | 2 | 2.5 | 417 | 0.0059952
0.5 | 9 | 2 | 3 | 500 | 0.006
0.5 | 9 | 2.2 | 0.5 | 85 | 0.0058824
0.5 | 9 | 2.2 | 1 | 170 | 0.0058824
0.5 | 9 | 2.2 | 1.5 | 256 | 0.0058594
0.5 | 9 | 2.2 | 2 | 341 | 0.0058651
0.5 | 9 | 2.2 | 2.5 | 426 | 0.0058685
0.5 | 9 | 2.2 | 3 | 511 | 0.0058708
0.5 | 9 | 2.4 | 0.5 | 87 | 0.0057471
0.5 | 9 | 2.4 | 1 | 174 | 0.0057471
0.5 | 9 | 2.4 | 1.5 | 261 | 0.0057471
0.5 | 9 | 2.4 | 2 | 348 | 0.0057471
0.5 | 9 | 2.4 | 2.5 | 435 | 0.0057471
0.5 | 9 | 2.4 | 3 | 522 | 0.0057471
0.5 | 9 | 2.6 | 0.5 | 89 | 0.005618
0.5 | 9 | 2.6 | 1 | 178 | 0.005618
0.5 | 9 | 2.6 | 1.5 | 267 | 0.005618
0.5 | 9 | 2.6 | 2 | 355 | 0.0056338
0.5 | 9 | 2.6 | 2.5 | 444 | 0.0056306
0.5 | 9 | 2.6 | 3 | 533 | 0.0056285
0.5 | 9 | 2.8 | 0.5 | 91 | 0.0054945
0.5 | 9 | 2.8 | 1 | 181 | 0.0055249
0.5 | 9 | 2.8 | 1.5 | 272 | 0.0055147
0.5 | 9 | 2.8 | 2 | 362 | 0.0055249
0.5 | 9 | 2.8 | 2.5 | 453 | 0.0055188
0.5 | 9 | 2.8 | 3 | 543 | 0.0055249
0.5 | 9 | 3 | 0.5 | 92 | 0.0054348
0.5 | 9 | 3 | 1 | 184 | 0.0054348
0.5 | 9 | 3 | 1.5 | 276 | 0.0054348
0.5 | 9 | 3 | 2 | 368 | 0.0054348
0.5 | 9 | 3 | 2.5 | 460 | 0.0054348
0.5 | 9 | 3 | 3 | 552 | 0.0054348
5 | 9 | 0.4 | 0.5 | 47 | 0.010638
5 | 9 | 0.4 | 1 | 93 | 0.010753
5 | 9 | 0.4 | 1.5 | 140 | 0.010714
5 | 9 | 0.4 | 2 | 186 | 0.010753
5 | 9 | 0.4 | 2.5 | 233 | 0.01073
5 | 9 | 0.4 | 3 | 279 | 0.010753
5 | 9 | 0.6 | 0.5 | 49 | 0.010204
5 | 9 | 0.6 | 1 | 97 | 0.010309
5 | 9 | 0.6 | 1.5 | 146 | 0.010274
5 | 9 | 0.6 | 2 | 194 | 0.010309
5 | 9 | 0.6 | 2.5 | 243 | 0.010288
5 | 9 | 0.6 | 3 | 291 | 0.010309
5 | 9 | 0.8 | 0.5 | 50 | 0.01
5 | 9 | 0.8 | 1 | 100 | 0.01
5 | 9 | 0.8 | 1.5 | 151 | 0.0099338
5 | 9 | 0.8 | 2 | 201 | 0.0099502
5 | 9 | 0.8 | 2.5 | 251 | 0.0099602
5 | 9 | 0.8 | 3 | 301 | 0.0099668
5 | 9 | 1 | 0.5 | 52 | 0.0096154
5 | 9 | 1 | 1 | 104 | 0.0096154
5 | 9 | 1 | 1.5 | 156 | 0.0096154
5 | 9 | 1 | 2 | 208 | 0.0096154
5 | 9 | 1 | 2.5 | 260 | 0.0096154
5 | 9 | 1 | 3 | 312 | 0.0096154
5 | 9 | 1.2 | 0.5 | 53 | 0.009434
5 | 9 | 1.2 | 1 | 107 | 0.0093458
5 | 9 | 1.2 | 1.5 | 160 | 0.009375
5 | 9 | 1.2 | 2 | 213 | 0.0093897
5 | 9 | 1.2 | 2.5 | 267 | 0.0093633
5 | 9 | 1.2 | 3 | 320 | 0.009375
5 | 9 | 1.4 | 0.5 | 55 | 0.0090909
5 | 9 | 1.4 | 1 | 110 | 0.0090909
5 | 9 | 1.4 | 1.5 | 165 | 0.0090909
5 | 9 | 1.4 | 2 | 219 | 0.0091324
5 | 9 | 1.4 | 2.5 | 274 | 0.0091241
5 | 9 | 1.4 | 3 | 329 | 0.0091185
5 | 9 | 1.6 | 0.5 | 56 | 0.0089286
5 | 9 | 1.6 | 1 | 112 | 0.0089286
5 | 9 | 1.6 | 1.5 | 169 | 0.0088757
5 | 9 | 1.6 | 2 | 225 | 0.0088889
5 | 9 | 1.6 | 2.5 | 281 | 0.0088968
5 | 9 | 1.6 | 3 | 337 | 0.0089021
5 | 9 | 1.8 | 0.5 | 58 | 0.0086207
5 | 9 | 1.8 | 1 | 115 | 0.0086957
5 | 9 | 1.8 | 1.5 | 173 | 0.0086705
5 | 9 | 1.8 | 2 | 230 | 0.0086957
5 | 9 | 1.8 | 2.5 | 288 | 0.0086806
5 | 9 | 1.8 | 3 | 345 | 0.0086957
5 | 9 | 2 | 0.5 | 59 | 0.0084746
5 | 9 | 2 | 1 | 118 | 0.0084746
5 | 9 | 2 | 1.5 | 177 | 0.0084746
5 | 9 | 2 | 2 | 235 | 0.0085106
5 | 9 | 2 | 2.5 | 294 | 0.0085034
5 | 9 | 2 | 3 | 353 | 0.0084986
5 | 9 | 2.2 | 0.5 | 60 | 0.0083333
5 | 9 | 2.2 | 1 | 120 | 0.0083333
5 | 9 | 2.2 | 1.5 | 181 | 0.0082873
5 | 9 | 2.2 | 2 | 241 | 0.0082988
5 | 9 | 2.2 | 2.5 | 301 | 0.0083056
5 | 9 | 2.2 | 3 | 361 | 0.0083102
5 | 9 | 2.4 | 0.5 | 61 | 0.0081967
5 | 9 | 2.4 | 1 | 123 | 0.0081301
5 | 9 | 2.4 | 1.5 | 184 | 0.0081522
5 | 9 | 2.4 | 2 | 245 | 0.0081633
5 | 9 | 2.4 | 2.5 | 307 | 0.0081433
5 | 9 | 2.4 | 3 | 368 | 0.0081522
5 | 9 | 2.6 | 0.5 | 63 | 0.0079365
5 | 9 | 2.6 | 1 | 125 | 0.008
5 | 9 | 2.6 | 1.5 | 188 | 0.0079787
5 | 9 | 2.6 | 2 | 250 | 0.008
5 | 9 | 2.6 | 2.5 | 313 | 0.0079872
5 | 9 | 2.6 | 3 | 375 | 0.008
5 | 9 | 2.8 | 0.5 | 64 | 0.0078125
5 | 9 | 2.8 | 1 | 127 | 0.007874
5 | 9 | 2.8 | 1.5 | 191 | 0.0078534
5 | 9 | 2.8 | 2 | 255 | 0.0078431
5 | 9 | 2.8 | 2.5 | 318 | 0.0078616
5 | 9 | 2.8 | 3 | 382 | 0.0078534
5 | 9 | 3 | 0.5 | 65 | 0.0076923
5 | 9 | 3 | 1 | 130 | 0.0076923
5 | 9 | 3 | 1.5 | 195 | 0.0076923
5 | 9 | 3 | 2 | 259 | 0.007722
5 | 9 | 3 | 2.5 | 324 | 0.007716
5 | 9 | 3 | 3 | 389 | 0.0077121
10 | 9 | 0.4 | 0.5 | 35 | 0.014286
10 | 9 | 0.4 | 1 | 70 | 0.014286
10 | 9 | 0.4 | 1.5 | 105 | 0.014286
10 | 9 | 0.4 | 2 | 139 | 0.014388
10 | 9 | 0.4 | 2.5 | 174 | 0.014368
10 | 9 | 0.4 | 3 | 209 | 0.014354
10 | 9 | 0.6 | 0.5 | 36 | 0.013889
10 | 9 | 0.6 | 1 | 73 | 0.013699
10 | 9 | 0.6 | 1.5 | 109 | 0.013761
10 | 9 | 0.6 | 2 | 145 | 0.013793
10 | 9 | 0.6 | 2.5 | 182 | 0.013736
10 | 9 | 0.6 | 3 | 218 | 0.013761
10 | 9 | 0.8 | 0.5 | 38 | 0.013158
10 | 9 | 0.8 | 1 | 75 | 0.013333
10 | 9 | 0.8 | 1.5 | 113 | 0.013274
10 | 9 | 0.8 | 2 | 151 | 0.013245
10 | 9 | 0.8 | 2.5 | 188 | 0.013298
10 | 9 | 0.8 | 3 | 226 | 0.013274
10 | 9 | 1 | 0.5 | 39 | 0.012821
10 | 9 | 1 | 1 | 78 | 0.012821
10 | 9 | 1 | 1.5 | 117 | 0.012821
10 | 9 | 1 | 2 | 156 | 0.012821
10 | 9 | 1 | 2.5 | 195 | 0.012821
10 | 9 | 1 | 3 | 234 | 0.012821
10 | 9 | 1.2 | 0.5 | 40 | 0.0125
10 | 9 | 1.2 | 1 | 80 | 0.0125
10 | 9 | 1.2 | 1.5 | 120 | 0.0125
10 | 9 | 1.2 | 2 | 160 | 0.0125
10 | 9 | 1.2 | 2.5 | 200 | 0.0125
10 | 9 | 1.2 | 3 | 240 | 0.0125
10 | 9 | 1.4 | 0.5 | 41 | 0.012195
10 | 9 | 1.4 | 1 | 82 | 0.012195
10 | 9 | 1.4 | 1.5 | 124 | 0.012097
10 | 9 | 1.4 | 2 | 165 | 0.012121
10 | 9 | 1.4 | 2.5 | 206 | 0.012136
10 | 9 | 1.4 | 3 | 247 | 0.012146
10 | 9 | 1.6 | 0.5 | 42 | 0.011905
10 | 9 | 1.6 | 1 | 84 | 0.011905
10 | 9 | 1.6 | 1.5 | 127 | 0.011811
10 | 9 | 1.6 | 2 | 169 | 0.011834
10 | 9 | 1.6 | 2.5 | 211 | 0.011848
10 | 9 | 1.6 | 3 | 253 | 0.011858
10 | 9 | 1.8 | 0.5 | 43 | 0.011628
10 | 9 | 1.8 | 1 | 86 | 0.011628
10 | 9 | 1.8 | 1.5 | 130 | 0.011538
10 | 9 | 1.8 | 2 | 173 | 0.011561
10 | 9 | 1.8 | 2.5 | 216 | 0.011574
10 | 9 | 1.8 | 3 | 259 | 0.011583
10 | 9 | 2 | 0.5 | 44 | 0.011364
10 | 9 | 2 | 1 | 88 | 0.011364
10 | 9 | 2 | 1.5 | 133 | 0.011278
10 | 9 | 2 | 2 | 177 | 0.011299
10 | 9 | 2 | 2.5 | 221 | 0.011312
10 | 9 | 2 | 3 | 265 | 0.011321
10 | 9 | 2.2 | 0.5 | 45 | 0.011111
10 | 9 | 2.2 | 1 | 90 | 0.011111
10 | 9 | 2.2 | 1.5 | 136 | 0.011029
10 | 9 | 2.2 | 2 | 181 | 0.01105
10 | 9 | 2.2 | 2.5 | 226 | 0.011062
10 | 9 | 2.2 | 3 | 271 | 0.01107
10 | 9 | 2.4 | 0.5 | 46 | 0.01087
10 | 9 | 2.4 | 1 | 92 | 0.01087
10 | 9 | 2.4 | 1.5 | 138 | 0.01087
10 | 9 | 2.4 | 2 | 184 | 0.01087
10 | 9 | 2.4 | 2.5 | 230 | 0.01087
10 | 9 | 2.4 | 3 | 276 | 0.01087
10 | 9 | 2.6 | 0.5 | 47 | 0.010638
10 | 9 | 2.6 | 1 | 94 | 0.010638
10 | 9 | 2.6 | 1.5 | 141 | 0.010638
10 | 9 | 2.6 | 2 | 187 | 0.010695
10 | 9 | 2.6 | 2.5 | 234 | 0.010684
10 | 9 | 2.6 | 3 | 281 | 0.010676
10 | 9 | 2.8 | 0.5 | 48 | 0.010417
10 | 9 | 2.8 | 1 | 96 | 0.010417
10 | 9 | 2.8 | 1.5 | 144 | 0.010417
10 | 9 | 2.8 | 2 | 191 | 0.010471
10 | 9 | 2.8 | 2.5 | 239 | 0.01046
10 | 9 | 2.8 | 3 | 287 | 0.010453
10 | 9 | 3 | 0.5 | 49 | 0.010204
10 | 9 | 3 | 1 | 97 | 0.010309
10 | 9 | 3 | 1.5 | 146 | 0.010274
10 | 9 | 3 | 2 | 195 | 0.010256
10 | 9 | 3 | 2.5 | 243 | 0.010288
10 | 9 | 3 | 3 | 292 | 0.010274
15 | 9 | 0.4 | 0.5 | 23 | 0.021739
15 | 9 | 0.4 | 1 | 47 | 0.021277
15 | 9 | 0.4 | 1.5 | 70 | 0.021429
15 | 9 | 0.4 | 2 | 93 | 0.021505
15 | 9 | 0.4 | 2.5 | 117 | 0.021368
15 | 9 | 0.4 | 3 | 140 | 0.021429
15 | 9 | 0.6 | 0.5 | 24 | 0.020833
15 | 9 | 0.6 | 1 | 49 | 0.020408
15 | 9 | 0.6 | 1.5 | 73 | 0.020548
15 | 9 | 0.6 | 2 | 97 | 0.020619
15 | 9 | 0.6 | 2.5 | 122 | 0.020492
15 | 9 | 0.6 | 3 | 146 | 0.020548
15 | 9 | 0.8 | 0.5 | 25 | 0.02
15 | 9 | 0.8 | 1 | 50 | 0.02
15 | 9 | 0.8 | 1.5 | 76 | 0.019737
15 | 9 | 0.8 | 2 | 101 | 0.019802
15 | 9 | 0.8 | 2.5 | 126 | 0.019841
15 | 9 | 0.8 | 3 | 151 | 0.019868
15 | 9 | 1 | 0.5 | 26 | 0.019231
15 | 9 | 1 | 1 | 52 | 0.019231
15 | 9 | 1 | 1.5 | 78 | 0.019231
15 | 9 | 1 | 2 | 104 | 0.019231
15 | 9 | 1 | 2.5 | 130 | 0.019231
15 | 9 | 1 | 3 | 156 | 0.019231
15 | 9 | 1.2 | 0.5 | 27 | 0.018519
15 | 9 | 1.2 | 1 | 53 | 0.018868
15 | 9 | 1.2 | 1.5 | 80 | 0.01875
15 | 9 | 1.2 | 2 | 107 | 0.018692
15 | 9 | 1.2 | 2.5 | 133 | 0.018797
15 | 9 | 1.2 | 3 | 160 | 0.01875
15 | 9 | 1.4 | 0.5 | 28 | 0.017857
15 | 9 | 1.4 | 1 | 55 | 0.018182
15 | 9 | 1.4 | 1.5 | 83 | 0.018072
15 | 9 | 1.4 | 2 | 110 | 0.018182
15 | 9 | 1.4 | 2.5 | 138 | 0.018116
15 | 9 | 1.4 | 3 | 165 | 0.018182
15 | 9 | 1.6 | 0.5 | 28 | 0.017857
15 | 9 | 1.6 | 1 | 56 | 0.017857
15 | 9 | 1.6 | 1.5 | 85 | 0.017647
15 | 9 | 1.6 | 2 | 113 | 0.017699
15 | 9 | 1.6 | 2.5 | 141 | 0.01773
15 | 9 | 1.6 | 3 | 169 | 0.017751
15 | 9 | 1.8 | 0.5 | 29 | 0.017241
15 | 9 | 1.8 | 1 | 58 | 0.017241
15 | 9 | 1.8 | 1.5 | 87 | 0.017241
15 | 9 | 1.8 | 2 | 115 | 0.017391
15 | 9 | 1.8 | 2.5 | 144 | 0.017361
15 | 9 | 1.8 | 3 | 173 | 0.017341
15 | 9 | 2 | 0.5 | 30 | 0.016667
15 | 9 | 2 | 1 | 59 | 0.016949
15 | 9 | 2 | 1.5 | 89 | 0.016854
15 | 9 | 2 | 2 | 118 | 0.016949
15 | 9 | 2 | 2.5 | 148 | 0.016892
15 | 9 | 2 | 3 | 177 | 0.016949
15 | 9 | 2.2 | 0.5 | 30 | 0.016667
15 | 9 | 2.2 | 1 | 60 | 0.016667
15 | 9 | 2.2 | 1.5 | 91 | 0.016484
15 | 9 | 2.2 | 2 | 121 | 0.016529
15 | 9 | 2.2 | 2.5 | 151 | 0.016556
15 | 9 | 2.2 | 3 | 181 | 0.016575
15 | 9 | 2.4 | 0.5 | 31 | 0.016129
15 | 9 | 2.4 | 1 | 61 | 0.016393
15 | 9 | 2.4 | 1.5 | 92 | 0.016304
15 | 9 | 2.4 | 2 | 123 | 0.01626
15 | 9 | 2.4 | 2.5 | 153 | 0.01634
15 | 9 | 2.4 | 3 | 184 | 0.016304
15 | 9 | 2.6 | 0.5 | 31 | 0.016129
15 | 9 | 2.6 | 1 | 63 | 0.015873
15 | 9 | 2.6 | 1.5 | 94 | 0.015957
15 | 9 | 2.6 | 2 | 125 | 0.016
15 | 9 | 2.6 | 2.5 | 157 | 0.015924
15 | 9 | 2.6 | 3 | 188 | 0.015957
15 | 9 | 2.8 | 0.5 | 32 | 0.015625
15 | 9 | 2.8 | 1 | 64 | 0.015625
15 | 9 | 2.8 | 1.5 | 96 | 0.015625
15 | 9 | 2.8 | 2 | 127 | 0.015748
15 | 9 | 2.8 | 2.5 | 159 | 0.015723
15 | 9 | 2.8 | 3 | 191 | 0.015707
15 | 9 | 3 | 0.5 | 33 | 0.015152
15 | 9 | 3 | 1 | 65 | 0.015385
15 | 9 | 3 | 1.5 | 98 | 0.015306
15 | 9 | 3 | 2 | 130 | 0.015385
15 | 9 | 3 | 2.5 | 163 | 0.015337
15 | 9 | 3 | 3 | 195 | 0.015385
20 | 9 | 0.4 | 0.5 | 18 | 0.027778
20 | 9 | 0.4 | 1 | 35 | 0.028571
20 | 9 | 0.4 | 1.5 | 53 | 0.028302
20 | 9 | 0.4 | 2 | 70 | 0.028571
20 | 9 | 0.4 | 2.5 | 88 | 0.028409
20 | 9 | 0.4 | 3 | 105 | 0.028571
20 | 9 | 0.6 | 0.5 | 18 | 0.027778
20 | 9 | 0.6 | 1 | 36 | 0.027778
20 | 9 | 0.6 | 1.5 | 55 | 0.027273
20 | 9 | 0.6 | 2 | 73 | 0.027397
20 | 9 | 0.6 | 2.5 | 91 | 0.027473
20 | 9 | 0.6 | 3 | 109 | 0.027523
20 | 9 | 0.8 | 0.5 | 19 | 0.026316
20 | 9 | 0.8 | 1 | 38 | 0.026316
20 | 9 | 0.8 | 1.5 | 57 | 0.026316
20 | 9 | 0.8 | 2 | 75 | 0.026667
20 | 9 | 0.8 | 2.5 | 94 | 0.026596
20 | 9 | 0.8 | 3 | 113 | 0.026549
20 | 9 | 1 | 0.5 | 20 | 0.025
20 | 9 | 1 | 1 | 39 | 0.025641
20 | 9 | 1 | 1.5 | 59 | 0.025424
20 | 9 | 1 | 2 | 78 | 0.025641
20 | 9 | 1 | 2.5 | 98 | 0.02551
20 | 9 | 1 | 3 | 117 | 0.025641
20 | 9 | 1.2 | 0.5 | 20 | 0.025
20 | 9 | 1.2 | 1 | 40 | 0.025
20 | 9 | 1.2 | 1.5 | 60 | 0.025
20 | 9 | 1.2 | 2 | 80 | 0.025
20 | 9 | 1.2 | 2.5 | 100 | 0.025
20 | 9 | 1.2 | 3 | 120 | 0.025
20 | 9 | 1.4 | 0.5 | 21 | 0.02381
20 | 9 | 1.4 | 1 | 41 | 0.02439
20 | 9 | 1.4 | 1.5 | 62 | 0.024194
20 | 9 | 1.4 | 2 | 82 | 0.02439
20 | 9 | 1.4 | 2.5 | 103 | 0.024272
20 | 9 | 1.4 | 3 | 123 | 0.02439
20 | 9 | 1.6 | 0.5 | 21 | 0.02381
20 | 9 | 1.6 | 1 | 42 | 0.02381
20 | 9 | 1.6 | 1.5 | 63 | 0.02381
20 | 9 | 1.6 | 2 | 84 | 0.02381
20 | 9 | 1.6 | 2.5 | 105 | 0.02381
20 | 9 | 1.6 | 3 | 126 | 0.02381
20 | 9 | 1.8 | 0.5 | 22 | 0.022727
20 | 9 | 1.8 | 1 | 43 | 0.023256
20 | 9 | 1.8 | 1.5 | 65 | 0.023077
20 | 9 | 1.8 | 2 | 86 | 0.023256
20 | 9 | 1.8 | 2.5 | 108 | 0.023148
20 | 9 | 1.8 | 3 | 129 | 0.023256
20 | 9 | 2 | 0.5 | 22 | 0.022727
20 | 9 | 2 | 1 | 44 | 0.022727
20 | 9 | 2 | 1.5 | 66 | 0.022727
20 | 9 | 2 | 2 | 88 | 0.022727
20 | 9 | 2 | 2.5 | 110 | 0.022727
20 | 9 | 2 | 3 | 132 | 0.022727
20 | 9 | 2.2 | 0.5 | 23 | 0.021739
20 | 9 | 2.2 | 1 | 45 | 0.022222
20 | 9 | 2.2 | 1.5 | 68 | 0.022059
20 | 9 | 2.2 | 2 | 90 | 0.022222
20 | 9 | 2.2 | 2.5 | 113 | 0.022124
20 | 9 | 2.2 | 3 | 135 | 0.022222
20 | 9 | 2.4 | 0.5 | 23 | 0.021739
20 | 9 | 2.4 | 1 | 46 | 0.021739
20 | 9 | 2.4 | 1.5 | 69 | 0.021739
20 | 9 | 2.4 | 2 | 92 | 0.021739
20 | 9 | 2.4 | 2.5 | 115 | 0.021739
20 | 9 | 2.4 | 3 | 138 | 0.021739
20 | 9 | 2.6 | 0.5 | 24 | 0.020833
20 | 9 | 2.6 | 1 | 47 | 0.021277
20 | 9 | 2.6 | 1.5 | 71 | 0.021127
20 | 9 | 2.6 | 2 | 94 | 0.021277
20 | 9 | 2.6 | 2.5 | 118 | 0.021186
20 | 9 | 2.6 | 3 | 141 | 0.021277
20 | 9 | 2.8 | 0.5 | 24 | 0.020833
20 | 9 | 2.8 | 1 | 48 | 0.020833
20 | 9 | 2.8 | 1.5 | 72 | 0.020833
20 | 9 | 2.8 | 2 | 95 | 0.021053
20 | 9 | 2.8 | 2.5 | 119 | 0.021008
20 | 9 | 2.8 | 3 | 143 | 0.020979
20 | 9 | 3 | 0.5 | 24 | 0.020833
20 | 9 | 3 | 1 | 49 | 0.020408
20 | 9 | 3 | 1.5 | 73 | 0.020548
20 | 9 | 3 | 2 | 97 | 0.020619
20 | 9 | 3 | 2.5 | 122 | 0.020492
20 | 9 | 3 | 3 | 146 | 0.020548

## Virus CT (hidden)
CT Tables
Viruses |  |  |  |  | Average K values for every Temp
Temperature | pH | Log Inactivation | CT | k | Temperature | k
0.5 | 6-9 | 2 | 6 | 0.33333 | 0.5 | 0.33333
0.5 | 6-9 | 3 | 9 | 0.33333 | 5 | 0.5
0.5 | 6-9 | 4 | 12 | 0.33333 | 10 | 0.69444
5 | 6-9 | 2 | 4 | 0.5 | 15 | 1
5 | 6-9 | 3 | 6 | 0.5 | 20 | 1.6111
5 | 6-9 | 4 | 8 | 0.5 | 25 | 2.3333
10 | 6-9 | 2 | 3 | 0.66667
10 | 6-9 | 3 | 4 | 0.75
10 | 6-9 | 4 | 6 | 0.66667
15 | 6-9 | 2 | 2 | 1
15 | 6-9 | 3 | 3 | 1
15 | 6-9 | 4 | 4 | 1
20 | 6-9 | 2 | 1 | 2
20 | 6-9 | 3 | 2 | 1.5
20 | 6-9 | 4 | 3 | 1.3333
25 | 6-9 | 2 | 1 | 2
25 | 6-9 | 3 | 1 | 3
25 | 6-9 | 4 | 2 | 2